# Spray Coating Operations

## General Requirements of Mechanical Ventilation Systems.

### Guide to Respiratory Protection at Work

(a) Design and Operation. The construction, installation, inspection, testing,

and maintenance of exhaust systems shall conform to all requirements. Additional guidance may be obtained from the American National Standard

Fundamentals Governing the Design and Operation of Local Exhaust Systems, ANSI Z9.2-1971 and the Standard for the Installation of Blower and Exhaust Systems, NFPA No. 91-1973.

(1) The exhaust system shall be so designed, constructed, maintained and

operated as to prevent harmful exposure by maintaining a volume and velocity of

exhaust air sufficient to gather dusts, fumes, mists, vapors or gases from said

equipment or process and to convey them to suitable points of safe disposal,

thereby preventing their dispersion in harmful quantities into the atmosphere of

work rooms or other places where persons are employed.

(2) Exhaust ducts, inlet ducts, and fan plenums shall be so designed,

constructed, and supported as to prevent collapse of the ducts and/or failure of

the supporting system.

(3) Exhaust ducts which convey dusts, fumes, and mists shall be provided with

inspection or clean-out doors at intervals not to exceed 12 feet of horizontal

running length for ducts up to 12 inches in diameter, but the distance may be

greater for larger ducts. A clean-out door or doors shall be provided for

servicing the fan and, where necessary, a drain shall be provided.

(4) Two or more operations shall not be connected to the same exhaust system

where the combination of substances removed may constitute a fire, explosion, or chemical reaction hazard in the duct system.

(5) The ventilation rate of every mechanical ventilation system used to prevent

harmful exposure shall be tested after initial installation, alterations, or

maintenance, and at least annually, by means of a pivot traverse of the exhaust

duct or equivalent measurements. Records of these tests shall be retained for at

least five years.

(b) Duration of Operations. The exhaust system shall be in operation continually

during all operations for which it is designed. The system shall continue to

operate for some time after the cessation of said operations, the length of time

to depend upon the individual circumstances and effectiveness of the ventilation

system.

(c) Disposal of Exhaust Materials.

(1) The air outlet from every dust separator/collector and the dusts, fumes,

mists, vapors or gases collected by an exhaust or ventilating system shall

discharge to the outside atmosphere, provided that the exhaust system shall

discharge to the outer air in such a manner that it will not cause a harmful

exposure in any accessible workplace. Collecting systems which return air to

work areas may be used if contaminants which accumulate in the work area do not result in harmful exposure to employees.

(2) The air exhausted from blast-cleaning equipment, grinding, buffing,

polishing equipment and all other equipment requiring exhausting of dust or

particulate shall be discharged through dust-collecting equipment. Dust and

refuse discharged from an exhaust system shall be disposed of in such a manner

that it will not result in harmful exposure to employees.

(d) Make-Up Air. Clean, fresh air, free of contamination from adjacent

industrial exhaust systems, chimneys, stacks, or vents, shall be supplied.

(1) The outside air supply shall enter the workroom in a manner which will not

reduce the effectiveness of any local exhaust systems.

(2) All seams and joints shall be sealed if negative pressure exists within

inlet ductwork such that there is a possibility of infiltration of harmful

quantities of gases, fumes, or mists from areas through which ductwork passes.

(3) Where the air supply is filtered, the filters shall be replaced or cleaned

regularly to prevent significant reductions in airflow. A pressure gauge shall

be installed to show the pressure drop across the filters. This gauge shall be

marked to show the pressure drop at which filters require cleaning or

replacement.

(4) Where make-up air is heated by combustion, except gas, the products of

combustion shall not be mixed with the make-up air and shall be vented to a

point remote from all points where make-up air enters the building. For gas

heating where combustion products are mixed with the make-up air, the following

must exist:

(A) The gas must be nontoxic and have a distinctive and strong enough odor to

warn workmen of its presence if unburned.

(B) The maximum rate of gas supply to the make-up air heater shall not yield in

excess of 2000 ppm of total combustible gas in the mixture upon flame failure.

(C) A fan shall be provided to remove the mixture of heated air and combustion

products from gas burner plenum chambers. (Title 24, T8-5143)

## Respiratory Protection.

(a) Permissible practice.

(1) In the control of those occupational diseases caused by breathing air contaminated with harmful dusts, fogs, fumes, mists, gases, smokes, sprays, or vapors, the primary objective shall be to prevent atmospheric contamination.

This shall be accomplished as far as feasible by accepted engineering control

measures (for example, enclosure or confinement of the operation, general and

local ventilation and substitution of less toxic materials). When effective

engineering controls are not feasible, or while they are being instituted,

appropriate respirators shall be used pursuant to this section.

(2) Respirators shall be provided by the company when such equipment is

necessary to protect the health of the employee. The company shall provide the

respirators which are applicable and suitable for the purpose intended. The

company shall be responsible for the establishment and maintenance of a

respiratory protection program which shall include the requirements outlined in

subsection (c).

(b) Definitions. The following definitions are important terms used in the respiratory protection standard in this section.

Air-purifying respirator means a respirator with an air-purifying filter,

cartridge or canister that removes specific air contaminants by passing ambient

air through the air-purifying element.

Assigned protection factor (APF) [Reserved]

Atmosphere-supplying respirator means a respirator that supplies the respirator

user with breathing air from a source independent of the ambient atmosphere, and includes supplied-air respirators (SARs) and self-contained breathing apparatus (SCBA) units.

Canister or cartridge means a container with a filter, sorbent, or catalyst, or

combination of these items, which removes specific contaminants from the air

passed through the container.

Demand respirator means an atmosphere-supplying respirator that admits breathing air to the facepiece only when a negative pressure is created inside the

facepiece by inhalation.

Emergency situation means any occurrence such as, but not limited to, equipment failure, rupture of containers, or failure of control equipment that may or does result in an uncontrolled significant release of an airborne contaminant.

Employee exposure means exposure to a concentration of an airborne contaminant that would occur if the employee were not using respiratory protection.

End-of-service-life indicator (ESLI) means a system that warns the respirator

user of the approach of the end of adequate respiratory protection, for example,

that the sorbent is approaching saturation or is no longer effective.

Escape-only respirator means a respirator intended to be used only for emergency exit.

Filter or air purifying element means a component used in respirators to remove

solid or liquid aerosols from the inspired air.

Filtering facepiece (dust mask) means a negative pressure particulate respirator

with a filter as an integral part of the facepiece or with the entire facepiece

composed of the filtering medium.

Fit factor means a quantitative estimate of the fit of a particular respirator

to a specific individual, and typically estimates the ratio of the concentration

of a substance in ambient air to its concentration inside the respirator when

worn.

Fit test means the use of a protocol to qualitatively or quantitatively evaluate

the fit of a respirator on an individual. (See also Qualitative fit test QLFT

and Quantitative fit test QNFT.)

Helmet means a rigid respiratory inlet covering that also provides head

protection against impact and penetration.

High efficiency particulate air (HEPA) filter means a filter that is at least

99.97% efficient in removing monodisperse particles of 0.3 micrometers in

diameter. The equivalent NIOSH 42 CFR 84 particulate filters are the N100, R100, and P100 filters.

Hood means a respiratory inlet covering that completely covers the head and neck and may also cover portions of the shoulders and torso.

Immediately dangerous to life or health (IDLH) means an atmosphere that poses an immediate threat to life, would cause irreversible adverse health effects, or

would impair an individual's ability to escape from a dangerous atmosphere.

Interior structural firefighting means the physical activity of fire

suppression, rescue or both, inside of buildings or enclosed structures which

are involved in a fire situation beyond the incipient stage.

Loose-fitting facepiece means a respiratory inlet covering that is designed to

form a partial seal with the face.

Maximum use concentration (MUC) [Reserved].

Negative pressure respirator (tight fitting) means a respirator in which the air

pressure inside the facepiece is negative during inhalation with respect to the

ambient air pressure outside the respirator.

Oxygen deficient atmosphere means an atmosphere with an oxygen content below 19.5% by volume.

Physician or other licensed health care professional (PLHCP) means an individual whose legally permitted scope of practice (i.e., license, registration, or

certification) allows him or her to independently provide, or be delegated the

responsibility to provide, some or all of the health care services required by

subsection (e).

Positive pressure respirator means a respirator in which the pressure inside the

respiratory inlet covering exceeds the ambient air pressure outside the

respirator.

Powered air-purifying respirator (PAPR) means an air-purifying respirator that

uses a blower to force the ambient air through air-purifying elements to the

inlet covering.

Pressure demand respirator means a positive pressure atmosphere-supplying

respirator that admits breathing air to the facepiece when the positive pressure

is reduced inside the facepiece by inhalation.

Qualitative fit test (QLFT) means a pass/fail fit test to assess the adequacy of

respirator fit that relies on the individual's response to the test agent.

Quantitative fit test (QNFT) means an assessment of the adequacy of respirator

fit by numerically measuring the amount of leakage into the respirator.

Respiratory inlet covering means that portion of a respirator that forms the

protective barrier between the user's respiratory tract and an air-purifying

device or breathing air source, or both. It may be a facepiece, helmet, hood,

suit or a mouthpiece respirator with nose clamp.

Self-contained breathing apparatus (SCBA) means an atmosphere-supplying

respirator for which the breathing air source is designed to be carried by the

user.

Service life means the period of time that a respirator, filter or sorbent, or

other respiratory equipment provides adequate protection to the wearer.

Supplied-air respirator (SAR) or airline respirator means an

atmosphere-supplying respirator for which the source of breathing air is not

designed to be carried by the user.

Tight-fitting facepiece means a respiratory inlet covering that forms a complete

seal with the face.

User seal check means an action conducted by the respirator user to determine if

the respirator is properly seated to the face.

(c) Respiratory protection program. This subsection requires the company to develop and implement a written respiratory protection program with required

worksite-specific procedures and elements for required respirator use. The

program must be administered by a suitably trained program administrator. In

addition, certain program elements may be required for voluntary use to prevent

potential hazards associated with the use of the respirator. The Small Entity

Compliance Guide contains criteria for the selection of a program administrator

and a sample program that meets the requirements of this subsection. Copies of

the Small Entity Compliance Guide will be available from the Occupational Safety

and Health Administration's Office of Publications, Room N 3101, 200

Constitution Avenue, NW, Washington, DC, 20210 (202-219-4667).

(1) In any workplace where respirators are necessary to protect the health of

the employee or whenever respirators are required by the company, the company shall establish and implement a written respiratory protection program with worksite-specific procedures. The program shall be updated as necessary to

reflect those changes in workplace conditions that affect respirator use. The

company shall include in the program the following provisions, as applicable:

(A) Procedures for selecting respirators for use in the workplace;

(B) Medical evaluations of employees required to use respirators;

(C) Fit testing procedures for tight-fitting respirators;

(D) Procedures for proper use of respirators in routine and reasonably

foreseeable emergency situations;

(E) Procedures and schedules for cleaning, disinfecting, storing, inspecting,

repairing, discarding, and otherwise maintaining respirators;

(F) Procedures to ensure adequate air quality, quantity, and flow of breathing

air for atmosphere-supplying respirators;

(G) Training of employees in the respiratory hazards to which they are

potentially exposed during routine and emergency situations;

(H) Training of employees in the proper use of respirators, including putting on

and removing them, any limitations on their use, and their maintenance; and

(I) Procedures for regularly evaluating the effectiveness of the program.

(2) Where respirator use is not required:

(A) A company may provide respirators at the request of employees or permit employees to use their own respirators, if the company determines that such respirator use will not in itself create a hazard. If the company determines that any voluntary respirator use is permissible, the company shall provide the respirator users with the information contained in Appendix D to this section ("Information for Employees Using Respirators When Not Required Under the Standard"); and

(B) In addition, the company must establish and implement those elements of a written respiratory protection program necessary to ensure that any employee using a respirator voluntarily is medically able to use that respirator, and that the respirator is cleaned, stored, and maintained so that its use does not present a health hazard to the user. Exception: Companies are not required to include in a written respiratory protection program those employees whose only use of respirators involves the voluntary use of filtering facepieces (dust masks).

(3) The company shall designate a program administrator who is qualified

by appropriate training or experience that is commensurate with the

complexity of the program to administer or oversee the respiratory

protection program and conduct the required evaluations of program

effectiveness.

(4) The company shall provide respirators, training, and medical

evaluations at no cost to the employee.

(d) Selection of respirators. This subsection requires the company to evaluate respiratory hazard(s) in the workplace, identify relevant workplace and user factors, and base respirator selection on these factors. The subsection also

specifies appropriately protective respirators for use in IDLH atmospheres, and

limits the selection and use of air-purifying respirators.

(1) General requirements.

(A) The company shall select and provide an appropriate respirator based

in the respiratory hazard(s) to which the worker is exposed and workplace

and user factors that affect respirator performance and reliability.

(B) The company shall select a NIOSH-certified respirator. The respirator

shall be used in compliance with the conditions of its certification.

(C) The company shall identify and evaluate the respiratory hazard(s) in

the workplace; this evaluation shall include a reasonable estimate of

employee exposures to respiratory hazard(s) and an identification of the

contaminant's chemical state and physical form. Where the company

cannot identify or reasonably estimate the employee exposure, the

company shall consider the atmosphere to be IDLH.

(D) The company shall select respirators from a sufficient number of

respirator models and sizes so that the respirator is acceptable to, and

correctly fits, the user.

(2) Respirators for IDLH atmospheres.

(A) The company shall provide the following respirators for employee use

in IDLH atmospheres:

1. A full facepiece pressure demand SCBA certified by NIOSH for a minimum

service life of thirty minutes, or

2. A combination full facepiece pressure demand supplied-air respirator (SAR)

with auxiliary self-contained air supply.

(B) Respirators provided only for escape from IDLH atmospheres shall be

NIOSH-certified for escape from the atmosphere in which they will be

used.

(C) All oxygen-deficient atmospheres shall be considered IDLH.

Exception: If the company demonstrates that, under all foreseeable conditions, the oxygen concentration can be maintained within the ranges specified in Table II (i.e., for the altitudes set out in the table), then any atmosphere-supplying respirator may be used.

(3) Respirators for atmospheres that are not IDLH.

(A) The company shall provide a respirator that is adequate to protect the health of the employee and ensure compliance with all other OSHA statutory and regulatory requirements, under routine and reasonably foreseeable emergency situations.

1. Assigned Protection Factors (APFs) [Reserved]

2. Maximum Use Concentration (MUC) [Reserved]

(B) The respirator selected shall be appropriate for the chemical state and

physical form of the contaminant.

(C) For protection against gases and vapors, the company shall provide:

1. An atmosphere-supplying respirator, or

2. An air-purifying respirator, provided that:

a. The respirator is equipped with an end-of-service-life indicator (ESLI)

certified by NIOSH for the contaminant; or

b. If there is no ESLI appropriate for conditions in the company's workplace,

the company implements a change schedule for canisters and cartridges that is

based on objective information or data that will ensure that canisters and

cartridges are changed before the end of their service life. The company shall

describe in the respirator program the information and data relied upon and the

basis for the canister and cartridge change schedule and the basis for reliance

on the data.

(D) For protection against particulates, the company shall provide:

1. An atmosphere-supplying respirator; or

2. An air-purifying respirator equipped with a filter certified by NIOSH under

30 CFR part 11 as a high efficiency particulate air (HEPA) filter, or an

air-purifying respirator equipped with a filter certified for particulates by

NIOSH under 42 CFR part 84; or

3. For contaminants consisting primarily of particles with mass median

aerodynamic diameters (MMAD) of at least 2 micrometers, an air-purifying

respirator equipped with any filter certified for particulates by NIOSH.

Table I.--Assigned Protection Factors [Reserved]

Table II

Altitude (ft.) Oxygen deficient Atmospheres

(% 02) for which the company may rely on atmosphere-supplying respirators

Less than 3,001............................................ 16.0-19.5

3,001-4,000................................................ 16.4-19.5

4,001-5,000................................................ 17.1-19.5

5,001-6,000................................................ 17.8-19.5

6,001-7,000................................................ 18.5-19.5

7,001-8,0001............................................... 19.3-19.5

1 Above 8,000 feet the exception does not apply. Oxygen-enriched breathing air

must be supplied above 14,000 feet.

(e) Medical evaluation. Using a respirator may place a physiological burden on employees that varies with the type of respirator worn, the job and workplace conditions in which the respirator is used, and the medical status of the

employee. Accordingly, this subsection specifies the minimum requirements for

medical evaluation that companies must implement to determine the employee's

ability to use a respirator.

(1) General. The company shall provide a medical evaluation to determine the

employee's ability to use a respirator, before the employee is fit tested or

required to use the respirator in the workplace. The company may discontinue an

employee's medical evaluations when the employee is no longer required to use a respirator.

(2) Medical evaluation procedures.

(A) The company shall identify a physician or other licensed health care

professional (PLHCP) to perform medical evaluations using a medical

questionnaire or an initial medical examination that obtains the same

information as the medical questionnaire.

(B) The medical evaluation shall obtain the information requested by the

questionnaire in Sections 1 and 2, Part A of Appendix C.

(3) Follow-up medical examination.

(A) The company shall ensure that a follow-up medical examination is provided

for an employee who gives a positive response to any question among questions 1 through 8 in Section 2, Part A of Appendix C or whose initial medical

examination demonstrates the need for a follow-up medical examination.

(B) The follow-up medical examination shall include any medical tests,

consultations, or diagnostic procedures that the PLHCP deems necessary to make a final determination.

(4) Administration of the medical questionnaire and examinations.

(A) The medical questionnaire and examinations shall be administered

confidentially during the employee's normal working hours or at a time and place

convenient to the employee. The medical questionnaire shall be administered in a manner that ensures that the employee understands its content.

(B) The company shall provide the employee with an opportunity to discuss the

questionnaire and examination results with the PLHCP.

(5) Supplemental information for the PLHCP.

(A) The following information must be provided to the PLHCP before the PLHCP

makes a recommendation concerning an employee's ability to use a respirator:

1. The type and weight of the respirator to be used by the employee;

2. The duration and frequency of respirator use (including use for rescue and

escape);

3. The expected physical work effort;

4. Additional protective clothing and equipment to be worn; and

5. Temperature and humidity extremes that may be encountered.

(B) Any supplemental information provided previously to the PLHCP regarding an

employee need not be provided for a subsequent medical evaluation if the

information and the PLHCP remain the same.

(C) The company shall provide the PLHCP with a copy of the written respiratory

protection program and a copy of this section.

Note to Subsection (e)(5)(C): When the company replaces a PLHCP, the company must ensure that the new PLHCP obtains this information, either by providing the documents directly to the PLHCP or having the documents transferred from the former PLHCP to the new PLHCP. However, OSHA does not expect companies to have employees medically reevaluated solely because a new PLHCP has been selected.

(6) Medical determination. In determining the employee's ability to use a

respirator, the company shall:

(A) Obtain a written recommendation regarding the employee's ability to use the

respirator from the PLHCP. The recommendation shall provide only the following

information:

1. Any limitations on respirator use related to the medical condition of the

employee, or relating to the workplace conditions in which the respirator will

be used, including whether or not the employee is medically able to use the

respirator;

2. The need, if any, for follow-up medical evaluations; and

3. A statement that the PLHCP has provided the employee with a copy of the

PLHCP's written recommendation.

(B) If the respirator is a negative pressure respirator and the PLHCP finds a

medical condition that may place the employee's health at increased risk if the

respirator is used, the company shall provide a PAPR if the PLHCP's medical

evaluation finds that the employee can use such a respirator; if a subsequent

medical evaluation finds that the employee is medically able to use a negative

pressure respirator, then the company is no longer required to provide a PAPR.

(7) Additional medical evaluations. At a minimum, the company shall provide

additional medical evaluations that comply with the requirements of this section

if:

(A) An employee reports medical signs or symptoms that are related to ability to

use a respirator;

(B) A PLHCP, supervisor, or the respirator program administrator informs the

company that an employee needs to be reevaluated;

(C) Information from the respiratory protection program, including observations

made during fit testing and program evaluation, indicates a need for employee

reevaluation; or

(D) A change occurs in workplace conditions (e.g., physical work effort,

protective clothing, temperature) that may result in a substantial increase in

the physiological burden placed on an employee.

(f) Fit testing. This subsection requires that, before an employee may be required to use any respirator with a negative or positive pressure

tight-fitting facepiece, the employee must be fit tested with the same make,

model, style, and size of respirator that will be used. This subsection

specifies the kinds of fit tests allowed, the procedures for conducting them,

and how the results of the fit tests must be used.

(1) The company shall ensure that employees using a tight-fitting facepiece

respirator passes an appropriate qualitative fit test (QLFT) or quantitative fit

test (QNFT) as stated in this subsection.

(2) The company shall ensure that an employee using a tight-fitting facepiece

respirator is fit tested prior to initial use of the respirator, whenever a

different respirator facepiece (size, style, model or make) is used, and at

least annually thereafter.

(3) The company shall conduct an additional fit test whenever the employee

reports, or the company, PLHCP, supervisor, or program administrator makes

visual observations of, changes in the employee's physical condition that could

affect respirator fit. Such conditions include, but are not limited to, facial

scarring, dental changes, cosmetic surgery, or an obvious change in body weight.

(4) If after passing a QLFT or QNFT, the employee subsequently notifies the

company, program administrator, supervisor, or PLHCP that the fit of the

respirator is unacceptable; the employee shall be given a reasonable opportunity

to select a different respirator facepiece and to be retested.

(5) The fit test shall be administered using an OSHA-accepted QLFT or QNFT

protocol. The OSHA-accepted QLFT and QNFT protocols and procedures are contained in Appendix A.

(6) QLFT may only be used to fit test negative pressure air-purifying

respirators that must achieve a fit factor of 100 or less.

(7) If the fit factor, as determined through an OSHA-accepted QNFT protocol, is

equal to or greater than 100 for tight-fitting half facepieces, or equal to or

greater than 500 for tight-fitting full facepieces, the QNFT has been passed

with that respirator.

(8) Fit testing of tight-fitting atmosphere-supplying respirators and

tight-fitting powered air-purifying respirators shall be accomplished by

performing quantitative or qualitative fit testing in the negative pressure

mode, regardless of the mode of operation (negative or positive pressure) that

is used for respiratory protection.

(A) Qualitative fit testing of these respirators shall be accomplished by

temporarily converting the respirator user's actual facepiece into a negative

pressure respirator with appropriate filters, or by using an identical negative

pressure air-purifying respirator facepiece with the same sealing surfaces as a

surrogate for the atmosphere-supplying or powered air-purifying respirator

facepiece.

(B) Quantitative fit testing of these respirators shall be accomplished by

modifying the facepiece to allow sampling inside the facepiece in the breathing

zone of the user, midway between the nose and mouth. This requirement shall be accomplished by installing a permanent sampling probe onto a surrogate

facepiece, or by using a sampling adapter designed to temporarily provide a

means of sampling air from inside the facepiece.

(C) Any modifications to the respirator facepiece for fit testing shall be

completely removed, and the facepiece restored to NIOSH-approved configuration, before that facepiece can be used in the workplace.

(g) Use of respirators. This subsection requires companies to establish and implement procedures for the proper use of respirators. These requirements

include prohibiting conditions that may result in facepiece seal leakage,

preventing employees from removing respirators in hazardous environments, taking actions to ensure continued effective respirator operation throughout the work shift, and establishing procedures for the use of respirators in IDLH

atmospheres or in interior structural firefighting situations.

(1) Facepiece seal protection.

(A) The company shall not permit respirators with tight-fitting facepieces to

be worn by employees who have:

1. Facial hair that comes between the sealing surface of the facepiece and the

face or that interferes with valve function; or

2. Any condition that interferes with the face-to-facepiece seal or valve

function.

(B) If an employee wears corrective glasses or goggles or other personal

protective equipment, the company shall ensure that such equipment is worn in a

manner that does not interfere with the seal of the facepiece to the face of the

user.

(C) For all tight-fitting respirators, the company shall ensure that employees

perform a user seal check each time they put on the respirator using the

procedures in Appendix B-1 or procedures recommended by the respirator

manufacturer that the company demonstrates are as effective as those in

Appendix B-1.

(2) Continuing respirator effectiveness.

(A) Appropriate surveillance shall be maintained of work area conditions and

degree of employee exposure or stress. When there is a change in work area

conditions or degree of employee exposure or stress that may affect respirator

effectiveness, the company shall reevaluate the continued effectiveness of the

respirator.

(B) The company shall ensure that employees leave the respirator use area:

1. To wash their faces and respirator facepieces as necessary to prevent eye or

skin irritation associated with respirator use; or

2. If they detect vapor or gas breakthrough, changes in breathing resistance, or

leakage of the facepiece; or

3. To replace the respirator or the filter, cartridge, or canister elements.

(C) If the employee detects vapor or gas breakthrough, changes in breathing

resistance, or leakage of the facepiece, the company must replace or repair the

respirator before allowing the employee to return to the work area.

(3) Procedures for IDLH atmospheres. For all IDLH atmospheres, the company

shall ensure that:

(A) One employee or, when needed, more than one employee is located outside the IDLH atmosphere;

(B) Visual, voice, or signal line communication is maintained between the

employee(s) in the IDLH atmosphere and the employee(s) located outside the IDLH atmosphere;

(C) The employee(s) located outside the IDLH atmosphere are trained and equipped to provide effective emergency rescue;

(D) The company or designee is notified before the employee(s) located outside

the IDLH atmosphere enters the IDLH atmosphere to provide emergency rescue;

(E) The company or designee authorized to do so by the company, once notified,

provides necessary assistance appropriate to the situation;

(F) Employee(s) located outside the IDLH atmospheres are equipped with:

1. Pressure demand or other positive pressure SCBAs, or a pressure demand or

other positive pressure supplied-air respirator with auxiliary SCBA; and either

2. Appropriate retrieval equipment for removing the employee(s) who enter(s)

these hazardous atmospheres where retrieval equipment would contribute to the

rescue of the employee(s) and would not increase the overall risk resulting from

entry; or

3. Equivalent means for rescue where retrieval equipment is not required under

subsection (g) (3) (F) 2.

(4) Procedures for interior structural firefighting. In addition to the

requirements set forth under subsection (g) (3), in interior structural fires,

the company shall ensure that:

(A) At least two employees enter the IDLH atmosphere and remain in visual or

voice contact with one another at all times;

(B) At least two employees are located outside the IDLH atmosphere; and

(C) All employees engaged in interior structural firefighting use SCBAs.

Note 1 to subsection (g): One of the two individuals located outside the IDLH

atmosphere may be assigned to an additional role, such as incident commander in charge of the emergency or safety officer, so long as this individual is able to

perform assistance or rescue activities without jeopardizing the safety or

health of any firefighter working at the incident.

Note 2 to subsection (g): Nothing in this section is meant to preclude

firefighters from performing emergency rescue activities before an entire team

has assembled.

(h) Maintenance and care of respirators. This subsection requires the company to provide for the cleaning and disinfecting, storage, inspection, and repair of

respirators used by employees.

(1) Cleaning and disinfecting. The company shall provide each respirator user

with a respirator that is clean, sanitary, and in good working order. The

company shall ensure that respirators are cleaned and disinfected using the

procedures in Appendix B-2, or procedures recommended by the respirator

manufacturer provided that such procedures are of equivalent effectiveness. The

respirators shall be cleaned and disinfected at the following intervals:

(A) Respirators issued for the exclusive use of an employee shall be cleaned and

disinfected as often as necessary to be maintained in a sanitary condition;

(B) Respirators issued to more than one employee shall be cleaned and

disinfected before being worn by different individuals;

(C) Respirators maintained for emergency use shall be cleaned and disinfected

after each use; and

(D) Respirators used in fit testing and training shall be cleaned and

disinfected after each use.

(2) Storage. The company shall ensure that respirators are stored as follows:

(A) All respirators shall be stored to protect them from damage, contamination,

dust, sunlight, extreme temperatures, excessive moisture, and damaging

chemicals, and they shall be packed or stored to prevent deformation of the

facepiece and exhalation valve.

(B) In addition to the requirements of subsection (h) (2) (A), emergency

respirators shall be:

1. Kept accessible to the work area;

2. Stored in compartments or in covers that are clearly marked as containing

emergency respirators; and

3. Stored in accordance with any applicable manufacturer instructions.

(3) Inspection.

(A) The company shall ensure that respirators are inspected as follows:

1. All respirators used in routine situations shall be inspected before each use

and during cleaning;

2. All respirators maintained for use in emergency situations shall be inspected

at least monthly and in accordance with the manufacturer's recommendations, and shall be checked for proper function before and after each use; and

3. Emergency escape-only respirators shall be inspected before being carried

into the workplace for use.

(B) The company shall ensure that respirator inspections include the following:

1. A check of respirator function, tightness of connections, and the condition

of the various parts including, but not limited to, the facepiece, head straps,

valves, connecting tube, and cartridges, canisters or filters; and

2. A check of elastomeric parts for pliability and signs of deterioration.

(C) In addition to the requirements of subsections (h) (3) (A) and (B),

self-contained breathing apparatus shall be inspected monthly. Air and oxygen

cylinders shall be maintained in a fully charged state and shall be recharged

when the pressure falls to 90% of the manufacturer's recommended pressure level.

The company shall determine that the regulator and warning devices function

properly.

(D) For respirators maintained for emergency use, the company shall:

1. Certify the respirator by documenting the date the inspection was performed,

the name (or signature) of the person who made the inspection, the findings,

required remedial action, and a serial number or other means of identifying the

inspected respirator; and

2. Provide this information on a tag or label that is attached to the storage

compartment for the respirator, is kept with the respirator, or is included in

inspection reports stored as paper or electronic files. This information shall

be maintained until replaced following a subsequent certification.

(4) Repairs. The company shall ensure that respirators that fail an inspection

or are otherwise found to be defective are removed from service, and are

discarded or repaired or adjusted in accordance with the following procedures:

(A) Repairs or adjustments to respirators are to be made only by persons

appropriately trained to perform such operations and shall use only the

respirator manufacturer's NIOSH-approved parts designed for the respirator;

(B) Repairs shall be made according to the manufacturer's recommendations and

specifications for the type and extent of repairs to be performed; and

(C) Reducing and admission valves, regulators, and alarms shall be adjusted or

repaired only by the manufacturer or a technician trained by the manufacturer.

(i) Breathing air quality and use. This subsection requires the company to provide employees using atmosphere-supplying respirators (supplied-air and SCBA) with breathing gases of high purity.

(1) The company shall ensure that compressed air, compressed oxygen, liquid

air, and liquid oxygen used for respiration accords with the following

specifications:

(A) Compressed and liquid oxygen shall meet the United States Pharmacopoeia

requirements for medical or breathing oxygen; and

(B) Compressed breathing air shall meet at least the requirements for Grade D

breathing air described in ANSI/Compressed Gas Association Commodity

Specification for Air, G-7.1-1989, to include:

1. Oxygen content (v/v) of 19.5-23.5%;

2. Hydrocarbon (condensed) content of 5 milligrams per cubic meter of air or

less;

3. Carbon monoxide (CO) content of 10 ppm or less;

4. Carbon dioxide content of 1,000 ppm or less; and

5. Lack of noticeable odor.

(2) The company shall ensure that compressed oxygen is not used in

atmosphere-supplying respirators that have previously used compressed air.

(3) The company shall ensure that oxygen concentrations greater than 23.5% are used only in equipment designed for oxygen service or distribution.

(4) The company shall ensure that cylinders used to supply breathing air to

respirators meet the following requirements:

(A) Cylinders are tested and maintained as prescribed in the Shipping Container

Specification Regulations of the Department of Transportation (49 CFR part 173

and part 178);

(B) Cylinders of purchased breathing air have a certificate of analysis from the

supplier that the breathing air meets the requirements for Grade D breathing

air; and

(C) The moisture content in the cylinder does not exceed a dew point of -50

deg.F (-45.6 deg.C) at 1 atmosphere pressure.

(5) The company shall ensure that compressors used to supply breathing air to

respirators are constructed and situated so as to:

(A) Prevent entry of contaminated air into the air-supply system;

(B) Minimize moisture content so that the dew point at 1 atmosphere pressure is

10 degrees F (-5.56 deg.C) below the ambient temperature;

(C) Have suitable in-line air-purifying sorbent beds and filters to further

ensure breathing air quality. Sorbent beds and filters shall be maintained and

replaced or refurbished periodically following the manufacturer's instructions.

(D) Have a tag containing the most recent change date and the signature of the

person authorized by the company to perform the change. The tag shall be

maintained at the compressor.

(6) For compressors that are not oil-lubricated, the company shall ensure that

carbon monoxide levels in the breathing air do not exceed 10 ppm.

(7) For oil-lubricated compressors, the company shall use a high-temperature or

carbon monoxide alarm, or both, to monitor carbon monoxide levels. If only

high-temperature alarms are used; the air supply shall be monitored at intervals

sufficient to prevent carbon monoxide in the breathing air from exceeding 10

ppm.

(8) The company shall ensure that breathing air couplings are incompatible with

outlets for nonrespirable worksite air or other gas systems. No asphyxiating

substance shall be introduced into breathing air lines.

(9) The company shall use breathing gas containers marked in accordance with

the NIOSH respirator certification standard, 42 CFR part 84.

(j) Identification of filters, cartridges, and canisters. The company shall

ensure that all filters, cartridges and canisters used in the workplace are

labeled and color coded with the NIOSH approval label and that the label is not

removed and remains legible.

(k) Training and information. This subsection requires the company to provide

effective training to employees who are required to use respirators. The

training must be comprehensive, understandable, and recur annually, and more

often if necessary. This subsection also requires the company to provide the

basic information on respirators in Appendix D to employees who wear respirators when not required by this section or by the company to do so.

(1) The company shall ensure that each employee can demonstrate knowledge of at least the following:

(A) Why the respirator is necessary and how improper fit, usage, or maintenance

can compromise the protective effect of the respirator;

(B) What the limitations and capabilities of the respirator are;

(C) How to use the respirator effectively in emergency situations, including

situations in which the respirator malfunctions;

(D) How to inspect, put on and remove, use, and check the seals of the

respirator;

(E) What the procedures are for maintenance and storage of the respirator;

(F) How to recognize medical signs and symptoms that may limit or prevent the

effective use of respirators; and

(G) The general requirements of this section.

(2) The training shall be conducted in a manner that is understandable to the

employee.

(3) The company shall provide the training prior to requiring the employee to

use a respirator in the workplace.

(4) An company who is able to demonstrate that a new employee has received

training within the last 12 months that addresses the elements specified in

subsection (k) (1) (A) through (G) is not required to repeat such training

provided that, as required by subsection (k) (1), the employee can demonstrate

knowledge of those element(s). Previous training not repeated initially by the

company must be provided no later than 12 months from the date of the previous

training.

(5) Retraining shall be administered annually, and when the following situations

occur:

(A) Changes in the workplace or the type of respirator render previous training

obsolete;

(B) Inadequacies in the employee's knowledge or use of the respirator indicate

that the employee has not retained the requisite understanding or skill; or

(C) Any other situation arises in which retraining appears necessary to ensure

safe respirator use.

(6) The basic advisory information on respirators, as presented in Appendix D,

shall be provided by the company in any written or oral format, to employees

who wear respirators when such use is not required by this section or by the

company.

(l) Program evaluation. This section requires the company to conduct evaluations of the workplace to ensure that the written respiratory protection program is being properly implemented, and to consult employees to ensure that

they are using the respirators properly.

(1) The company shall conduct evaluations of the workplace as necessary to

ensure that the provisions of the current written program are being effectively

implemented and that it continues to be effective.

(2) The company shall regularly consult employees required to use respirators

to assess the employees' views on program effectiveness and to identify any

problems. Any problems that are identified during this assessment shall be

corrected. Factors to be assessed include, but are not limited to:

(A) Respirator fit (including the ability to use the respirator without

interfering with effective workplace performance);

(B) Appropriate respirator selection for the hazards to which the employee is

exposed;

(C) Proper respirator use under the workplace conditions the employee

encounters; and

(D) Proper respirator maintenance.

(m) Recordkeeping. This section requires the company to establish and retain

written information regarding medical evaluations, fit testing, and the

respirator program. This information will facilitate employee involvement in the

respirator program, assist the company in auditing the adequacy of the program,

and provide a record for compliance determinations by OSHA.

(1) Medical evaluation. Records of medical evaluations required by this section

must be retained and made available in accordance with section 3204.

(2) Fit testing.

(A) The company shall establish a record of the qualitative and quantitative

fit tests administered to an employee including:

1. The name or identification of the employee tested;

2. Type of fit test performed;

3. Specific make, model, style, and size of respirator tested;

4. Date of test; and

5. The pass/fail results for QLFTs or the fit factor and strip chart recording

or other recording of the test results for QNFTs.

(B) Fit test records shall be retained for respirator users until the next fit

test is administered.

(3) A written copy of the current respirator program shall be retained by the

company.

(4) Written materials required to be retained under this subsection shall be

made available upon request to affected employees and to the Chief or designee

for examination and copying.

(n) Dates.

(1) Effective date. This section is effective November 23, 1998. The obligations

imposed by this section commence on the effective date unless otherwise noted in this subsection. Compliance with obligations that do not commence on the

effective date shall occur no later than the applicable start-up date.

(2) Compliance dates. All obligations of this section commence on the effective

date except as follows:

(A) The determination that respirator use is required (subsection (a)) shall be

completed no later than 150 days from the effective date.

(B) Compliance with provisions of this section for all other provisions shall be

completed no later than 180 days from the effective date.

(3) Existing Respiratory Protection Programs. If, in the 12 month period

preceding the effective date, the company has conducted annual respirator

training, fit testing, respirator program evaluation, or medical evaluations,

the company may use the results of those activities to comply with the

corresponding provisions of this section, providing that these activities were

conducted in a manner that meets the requirements of this section.

(o) Appendices. Compliance with Appendix A, Appendix B-1, Appendix B-2, Appendix C and Appendix D is mandatory.

## Appendix A: Fit Testing Procedures (Mandatory)

## Part I. OSHA-Accepted Fit Test Protocols

A. Fit Testing Procedures--General Requirements. The company shall conduct fit testing using the following procedures. The requirements in this appendix apply

to all OSHA-accepted fit test methods, both QLFT and QNFT.

1. The test subject shall be allowed to pick the most acceptable respirator from

a sufficient number of respirator models and sizes so that the respirator is

acceptable to, and correctly fits, the user.

2. Prior to the selection process, the test subject shall be shown how to put on

a respirator, how it should be positioned on the face, how to set strap tension

and how to determine an acceptable fit. A mirror shall be available to assist

the subject in evaluating the fit and positioning of the respirator. This

instruction may not constitute the subject's formal training on respirator use,

because it is only a review.

3. The test subject shall be informed that he/she is being asked to select the

respirator that provides the most acceptable fit. Each respirator represents a

different size and shape, and if fitted and used properly, will provide adequate

protection.

4. The test subject shall be instructed to hold each chosen facepiece up to the

face and eliminate those that obviously do not give an acceptable fit.

5. The more acceptable facepieces are noted in case the one selected proves

unacceptable; the most comfortable mask is donned and worn at least five minutes to assess comfort. Assistance in assessing comfort can be given by discussing the points in the following item A.6. If the test subject is not familiar with using a particular respirator, the test subject shall be directed to don the

mask several times and to adjust the straps each time to become adept at setting

proper tension on the straps.

6. Assessment of comfort shall include a review of the following points with the

test subject and allowing the test subject adequate time to determine the

comfort of the respirator:

(a) Position of the mask on the nose

(b) Room for eye protection

(c) Room to talk

(d) Position of mask on face and cheeks

7. The following criteria shall be used to help determine the adequacy of the

respirator fit:

(a) Chin properly placed;

(b) Adequate strap tension, not overly tightened;

(c) Fit across nose bridge;

(d) Respirator of proper size to span distance from nose to chin;

(e) Tendency of respirator to slip;

(f) Self-observation in mirror to evaluate fit and respirator position.

8. The test subject shall conduct a user seal check, either the negative and

positive pressure seal checks described in Appendix B-1 or those recommended by the respirator manufacturer which provide equivalent protection to the

procedures in Appendix B-1. Before conducting the negative and positive pressure checks, the subject shall be told to seat the mask on the face by moving the head from side-to-side and up and down slowly while taking in a few slow deep breaths. Another facepiece shall be selected and retested if the test subject

fails the user seal check tests.

9. The test shall not be conducted if there is any hair growth between the skin and the facepiece sealing surface, such as stubble beard growth, beard, mustache or sideburns which cross the respirator sealing surface. Any type of apparel which interferes with a satisfactory fit shall be altered or removed.

10. If a test subject exhibits difficulty in breathing during the tests, she or

he shall be referred to a physician or other licensed health care professional,

as appropriate, to determine whether the test subject can wear a respirator

while performing her or his duties.

11. If the employee finds the fit of the respirator unacceptable, the test

subject shall be given the opportunity to select a different respirator and to

be retested.

12. Exercise regimen. Prior to the commencement of the fit test, the test

subject shall be given a description of the fit test and the test subject's

responsibilities during the test procedure. The description of the process shall

include a description of the test exercises that the subject will be performing.

The respirator to be tested shall be worn for at least 5 minutes before the

start of the fit test.

13. The fit test shall be performed while the test subject is wearing any

applicable safety equipment that may be worn during actual respirator use which

could interfere with respirator fit.

14. Test Exercises.

(a) The following test exercises are to be performed for all fit testing methods

prescribed in this appendix, except for the CNP method. A separate fit testing

exercise regimen is contained in the CNP protocol. The test subject shall

perform exercises, in the test environment, in the following manner:

(1) Normal breathing. In a normal standing position, without talking, the

subject shall breathe normally.

(2) Deep breathing. In a normal standing position, the subject shall breathe

slowly and deeply, taking caution so as not to hyperventilate.

(3) Turning head side to side. Standing in place, the subject shall slowly turn

his/her head from side to side between the extreme positions on each side. The

head shall be held at each extreme momentarily so the subject can inhale at each side.

(4) Moving head up and down. Standing in place, the subject shall slowly move

his/her head up and down. The subject shall be instructed to inhale in the up

position (i.e., when looking toward the ceiling).

(5) Talking. The subject shall talk out loud slowly and loud enough so as to be

heard clearly by the test conductor. The subject can read from a prepared text

such as the Rainbow Passage, count backward from 100, or recite a memorized poem or song.

Rainbow Passage

When the sunlight strikes raindrops in the air, they act like a prism and form a

rainbow. The rainbow is a division of white light into many beautiful colors.

These take the shape of a long round arch, with its path high above, and its two

ends apparently beyond the horizon. There is, according to legend, a boiling pot

of gold at one end. People look, but no one ever finds it. When a man looks for

something beyond reach, his friends say he is looking for the pot of gold at the

end of the rainbow.

(6) Grimace. The test subject shall grimace by smiling or frowning. (This

applies only to QNFT testing; it is not performed for QLFT)

(7) Bending over. The test subject shall bend at the waist as if he/she were to

touch his/her toes. Jogging in place shall be substituted for this exercise in

those test environments such as shroud type QNFT or QLFT units that do not

permit bending over at the waist.

(8) Normal breathing. Same as exercise (1).

(b) Each test exercise shall be performed for one minute except for the grimace

exercise which shall be performed for 15 seconds. The test subject shall be

questioned by the test conductor regarding the comfort of the respirator upon

completion of the protocol. If it has become unacceptable, another model of

respirator shall be tried. The respirator shall not be adjusted once the fit

test exercises begin. Any adjustment voids the test, and the fit test must be

repeated.

## B. Qualitative Fit Test (QLFT) Protocols

1. General

(a) The company shall ensure that persons administering QLFT are able to

prepare test solutions, calibrate equipment and perform tests properly,

recognize invalid tests, and ensure that test equipment is in proper working

order.

(b) The company shall ensure that QLFT equipment is kept clean and well

maintained so as to operate within the parameters for which it was designed.

2. Isoamyl Acetate Protocol

Note: This protocol is not appropriate to use for the fit testing of particulate

respirators. If used to fit test particulate respirators, the respirator must be

equipped with an organic vapor filter.

(a) Odor Threshold Screening. Odor threshold screening, performed without

wearing a respirator, is intended to determine if the individual tested can

detect the odor of isoamyl acetate at low levels.

(1) Three 1 liter glass with metal lids are required.

(2) Odor-free water (e.g., distilled or spring water) at approximately 25 deg. C

(77 deg. F) shall be used for the solutions.

(3) The isoamyl acetate (IAA) (also known at isopentyl acetate) stock solution

is prepared by adding 1 ml of pure IAA to 800 ml of odor-free water in a 1 liter

jar, closing the lid and shaking for 30 seconds. A new solution shall be

prepared at least weekly.

(4) The screening test shall be conducted in a room separate from the room used

for actual fit testing. The two rooms shall be well-ventilated to prevent the

odor of IAA from becoming evident in the general room air where testing takes

place.

(5) The odor test solution is prepared in a second jar by placing 0.4 ml of the

stock solution into 500 ml of odor-free water using a clean dropper or pipette.

The solution shall be shaken for 30 seconds and allowed to stand for two to

three minutes so that the IAA concentration above the liquid may reach

equilibrium. This solution shall be used for only one day.

(6) A test blank shall be prepared in a third jar by adding 500 cc of odor-free

water.

(7) The odor test and test blank jar lids shall be labeled (e.g., 1 and 2) for

jar identification. Labels shall be placed on the lids so that they can be

peeled off periodically and switched to maintain the integrity of the test.

(8) The following instruction shall be typed on a card and placed on the table

in front of the two test jars (i.e., 1 and 2): "The purpose of this test is to

determine if you can smell banana oil at a low concentration. The two bottles in

front of you contain water. One of these bottles also contains a small amount of

banana oil. Be sure the covers are on tight, and then shake each bottle for two

seconds. Unscrew the lid of each bottle, one at a time, and sniff at the mouth

of the bottle. Indicate to the test conductor which bottle contains banana oil."

(9) The mixtures used in the IAA odor detection test shall be prepared in an

area separate from where the test is performed, in order to prevent olfactory

fatigue in the subject.

(10) If the test subject is unable to correctly identify the jar containing the

odor test solution, the IAA qualitative fit test shall not be performed.

(11) If the test subject correctly identifies the jar containing the odor test

solution, the test subject may proceed to respirator selection and fit testing.

(b) Isoamyl Acetate Fit Test

(1) The fit test chamber shall be a clear 55-gallon drum liner suspended

inverted over a 2-foot diameter frame so that the top of the chamber is about 6

inches above the test subject's head. If no drum liner is available, a similar

chamber shall be constructed using plastic sheeting. The inside top center of

the chamber shall have a small hook attached.

(2) Each respirator used for the fitting and fit testing shall be equipped with

organic vapor cartridges or offer protection against organic vapors.

(3) After selecting, donning, and properly adjusting a respirator, the test

subject shall wear it to the fit testing room. This room shall be separate from

the room used for odor threshold screening and respirator selection, and shall

be well-ventilated, as by an exhaust fan or lab hood, to prevent general room

contamination.

(4) A copy of the test exercises and any prepared text from which the subject is

to read shall be taped to the inside of the test chamber.

(5) Upon entering the test chamber, the test subject shall be given a 6-inch by

5-inch piece of paper towel, or other porous, absorbent, single-ply material,

folded in half and wetted with 0.75 ml of pure IAA. The test subject shall hang

the wet towel on the hook at the top of the chamber. An IAA test swab or ampule

may be substituted for the IAA wetted paper towel provided it has been

demonstrated that the alternative IAA source will generate an IAA test

atmosphere with a concentration equivalent to that generated by the paper towel

method.

(6) Allow two minutes for the IAA test concentration to stabilize before

starting the fit test exercises. This would be an appropriate time to talk with

the test subject; to explain the fit test, the importance of his/her

cooperation and the purpose for the test exercises; or to demonstrate some of

the exercises.

(7) If at any time during the test, the subject detects the banana-like odor of

IAA, the test is failed. The subject shall quickly exit from the test chamber

and leave the test area to avoid olfactory fatigue.

(8) If the test is failed, the subject shall return to the selection room and

remove the respirator. The test subject shall repeat the odor sensitivity test,

select and put on another respirator, return to the test area and again begin

the fit test procedure described in (b) (1) through (7) above. The process

continues until a respirator that fits well has been found. Should the odor

sensitivity test be failed, the subject shall wait at least 5 minutes before

retesting. Odor sensitivity will usually have returned by this time.

(9) If the subject passes the test, the efficiency of the test procedure shall

be demonstrated by having the subject break the respirator face seal and take a

breath before exiting the chamber.

(10) When the test subject leaves the chamber, the subject shall remove the

saturated towel and return it to the person conducting the test, so that there

is no significant IAA concentration buildup in the chamber during subsequent

tests. The used towels shall be kept in a self-sealing plastic bag to keep the

test area from being contaminated.

3. Saccharin Solution Aerosol Protocol. The entire screening and testing

procedure shall be explained to the test subject prior to the conduct of the

screening test.

(a) Taste threshold screening. The saccharin taste threshold screening,

performed without wearing a respirator, is intended to determine whether the

individual being tested can detect the taste of saccharin.

(1) During threshold screening as well as during fit testing, subjects shall

wear an enclosure about the head and shoulders that is approximately 12 inches

in diameter by 14 inches tall with at least the front portion clear and that

allows free movements of the head when a respirator is worn. An enclosure

substantially similar to the 3M hood assembly, parts # FT 14 and # FT 15

combined, is adequate.

(2) The test enclosure shall have a 3/4-inch (1.9 cm) hole in front of the test

subject's nose and mouth area to accommodate the nebulizer nozzle.

(3) The test subject shall don the test enclosure. Throughout the threshold

screening test, the test subject shall breathe through his/her slightly open

mouth with tongue extended. The subject is instructed to report when he/she

detects a sweet taste.

(4) Using a DeVilbiss Model 40 Inhalation Medication Nebulizer or equivalent,

the test conductor shall spray the threshold check solution into the enclosure.

The nozzle is directed away from the nose and mouth of the person. This

nebulizer shall be clearly marked to distinguish it from the fit test solution

nebulizer.

(5) The threshold check solution is prepared by dissolving 0.83 gram of sodium

saccharin USP in 100 ml of warm water. It can be prepared by putting 1 ml of the

fit test solution (see (b) (5) below) in 100 ml of distilled water.

(6) To produce the aerosol, the nebulizer bulb is firmly squeezed so that it

collapses completely, then released and allowed to fully expand.

(7) Ten squeezes are repeated rapidly and then the test subject is asked whether

the saccharin can be tasted. If the test subject reports tasting the sweet taste

during the ten squeezes, the screening test is completed. The taste threshold is

noted as ten regardless of the number of squeezes actually completed.

(8) If the first response is negative, ten more squeezes are repeated rapidly

and the test subject is again asked whether the saccharin is tasted. If the test

subject reports tasting the sweet taste during the second ten squeezes, the

screening test is completed. The taste threshold is noted as twenty regardless

of the number of squeezes actually completed.

(9) If the second response is negative, ten more squeezes are repeated rapidly

and the test subject is again asked whether the saccharin is tasted. If the test

subject reports tasting the sweet taste during the third set of ten squeezes,

the screening test is completed. The taste threshold is noted as thirty

regardless of the number of squeezes actually completed.

(10) The test conductor will take note of the number of squeezes required to

solicit a taste response.

(11) If the saccharin is not tasted after 30 squeezes (step 10), the test

subject is unable to taste saccharin and may not perform the saccharin fit test.

Note to subsection 3. (a): If the test subject eats or drinks something sweet

before the screening test, he/she may be unable to taste the weak saccharin

solution.

(12) If a taste response is elicited, the test subject shall be asked to take

note of the taste for reference in the fit test.

(13) Correct use of the nebulizer means that approximately 1 ml of liquid is

used at a time in the nebulizer body.

(14) The nebulizer shall be thoroughly rinsed in water, shaken dry, and refilled

at least each morning and afternoon or at least every four hours.

(b) Saccharin solution aerosol fit test procedure.

(1) The test subject may not eat, drink (except plain water), smoke, or chew gum

for 15 minutes before the test.

(2) The fit test uses the same enclosure described in 3. (a) above.

(3) The test subject shall don the enclosure while wearing the respirator

selected in section I. A. of this appendix. The respirator shall be properly

adjusted and equipped with a particulate filter(s).

(4) A second DeVilbiss Model 40 Inhalation Medication Nebulizer or equivalent is

used to spray the fit test solution into the enclosure. This nebulizer shall be

clearly marked to distinguish it from the screening test solution nebulizer.

(5) The fit test solution is prepared by adding 83 grams of sodium saccharin to

100 ml of warm water.

(6) As before, the test subject shall breathe through the slightly open mouth

with tongue extended, and report if he/she tastes the sweet taste of saccharin.

(7) The nebulizer is inserted into the hole in the front of the enclosure and an

initial concentration of saccharin fit test solution is sprayed into the

enclosure using the same number of squeezes (either 10, 20 or 30 squeezes) based

on the number of squeezes required to elicit a taste response as noted during

the screening test. A minimum of 10 squeezes is required.

(8) After generating the aerosol, the test subject shall be instructed to

perform the exercises in section I. A. 14. of this appendix.

(9) Every 30 seconds the aerosol concentration shall be replenished using one

half the original number of squeezes used initially (e.g., 5, 10 or 15).

(10) The test subject shall indicate to the test conductor if at any time during

the fit test the taste of saccharin is detected. If the test subject does not

report tasting the saccharin, the test is passed.

(11) If the taste of saccharin is detected, the fit is deemed unsatisfactory and

the test is failed. A different respirator shall be tried and the entire test

procedure is repeated (taste threshold screening and fit testing).

(12) Since the nebulizer has a tendency to clog during use, the test operator

must make periodic checks of the nebulizer to ensure that it is not clogged. If

clogging is found at the end of the test session, the test is invalid.

4. BitrexTM (Denatonium Benzoate) Solution Aerosol Qualitative Fit Test

Protocol. The BitrexTM (Denatonium benzoate) solution aerosol QLFT protocol uses

the published saccharin test protocol because that protocol is widely accepted.

Bitrex is routinely used as a taste aversion agent in household liquids which

children should not be drinking and is endorsed by the American Medical

Association, the National Safety Council, and the American Association of Poison

Control Centers. The entire screening and testing procedure shall be explained

to the test subject prior to the conduct of the screening test.

(a) Taste Threshold Screening. The Bitrex taste threshold screening, performed

without wearing a respirator, is intended to determine whether the individual

being tested can detect the taste of Bitrex.

(1) During threshold screening as well as during fit testing, subjects shall

wear an enclosure about the head and shoulders that is approximately 12 inches

(30.5 cm) in diameter by 14 inches (35.6 cm) tall. The front portion of the

enclosure shall be clear from the respirator and allow free movement of the head

when a respirator is worn. An enclosure substantially similar to the 3M hood

assembly, parts #14 and #15 combined, is adequate.

(2) The test enclosure shall have a 3/4 inch (1.9 cm) hole in front of the test

subject's nose and mouth area to accommodate the nebulizer nozzle.

(3) The test subject shall don the test enclosure. Throughout the threshold

screening test, the test subject shall breathe through his or her slightly open

mouth with tongue extended. The subject is instructed to report when he/she

detects a bitter taste.

(4) Using a DeVilbiss Model 40 Inhalation Medication Nebulizer or equivalent,

the test conductor shall spray the Threshold Check Solution into the enclosure.

This Nebulizer shall be clearly marked to distinguish it from the fit test

solution nebulizer.

(5) The Threshold Check Solution is prepared by adding 13.5 milligrams of Bitrex

to 100 ml of 5% salt (NaCl) solution in distilled water.

(6) To produce the aerosol, the nebulizer bulb is firmly squeezed so that the

bulb collapses completely, and is then released and allowed to fully expand.

(7) An initial ten squeezes are repeated rapidly and then the test subject is

asked whether the Bitrex can be tasted. If the test subject reports tasting the

bitter taste during the ten squeezes, the screening test is completed. The taste

threshold is noted as ten regardless of the number of squeezes actually

completed.

(8) If the first response is negative, ten more squeezes are repeated rapidly

and the test subject is again asked whether the Bitrex is tasted. If the test

subject reports tasting the bitter taste during the second ten squeezes, the

screening test is completed. The taste threshold is noted as twenty regardless

of the number of squeezes actually completed.

(9) If the second response is negative, ten more squeezes are repeated rapidly

and the test subject is again asked whether the Bitrex is tasted. If the test

subject reports tasting the bitter taste during the third set of ten squeezes,

the screening test is completed. The taste threshold is noted as thirty

regardless of the number of squeezes actually completed.

(10) The test conductor will take note of the number of squeezes required to

solicit a taste response.

(11) If the Bitrex is not tasted after 30 squeezes (step 10), the test subject

is unable to taste Bitrex and may not perform the Bitrex fit test.

(12) If a taste response is elicited, the test subject shall be asked to take

note of the taste for reference in the fit test.

(13) Correct use of the nebulizer means that approximately 1 ml of liquid is

used at a time in the nebulizer body.

(14) The nebulizer shall be thoroughly rinsed in water, shaken to dry, and

refilled at least each morning and afternoon or at least every four hours.

(b) Bitrex Solution Aerosol Fit Test Procedure.

(1) The test subject may not eat, drink (except plain water), smoke, or chew gum

for 15 minutes before the test.

(2) The fit test uses the same enclosure as that described in 4. (a) above.

(3) The test subject shall don the enclosure while wearing the respirator

selected according to section I. A. of this appendix. The respirator shall be

properly adjusted and equipped with any type particulate filter(s).

(4) A second DeVilbiss Model 40 Inhalation Medication Nebulizer or equivalent is

used to spray the fit test solution into the enclosure. This nebulizer shall be

clearly marked to distinguish it from the screening test solution nebulizer.

(5) The fit test solution is prepared by adding 337.5 mg of Bitrex to 200 ml of

a 5% salt (NaCl) solution in warm water.

(6) As before, the test subject shall breathe through his or her slightly open

mouth with tongue extended, and be instructed to report if he/she tastes the

bitter taste of Bitrex.

(7) The nebulizer is inserted into the hole in the front of the enclosure and an

initial concentration of the fit test solution is sprayed into the enclosure

using the same number of squeezes (either 10, 20 or 30 squeezes) based on the

number of squeezes required to elicit a taste response as noted during the

screening test.

(8) After generating the aerosol, the test subject shall be instructed to

perform the exercises in section I. A. 14. of this appendix.

(9) Every 30 seconds the aerosol concentration shall be replenished using one

half the number of squeezes used initially (e.g., 5, 10 or 15).

(10) The test subject shall indicate to the test conductor if at any time during

the fit test the taste of Bitrex is detected. If the test subject does not

report tasting the Bitrex, the test is passed.

(11) If the taste of Bitrex is detected, the fit is deemed unsatisfactory and

the test is failed. A different respirator shall be tried and the entire test

procedure is repeated (taste threshold screening and fit testing).

5. Irritant Smoke (Stannic Chloride) Protocol. This qualitative fit test uses a

person's response to the irritating chemicals released in the "smoke" produced

by a stannic chloride ventilation smoke tube to detect leakage into the

respirator.

(a) General Requirements and Precautions

(1) The respirator to be tested shall be equipped with high efficiency

particulate air (HEPA) or P100 series filter(s).

(2) Only stannic chloride smoke tubes shall be used for this protocol.

(3) No form of test enclosure or hood for the test subject shall be used.

(4) The smoke can be irritating to the eyes, lungs, and nasal passages. The test

conductor shall take precautions to minimize the test subject's exposure to

irritant smoke. Sensitivity varies, and certain individuals may respond to a

greater degree to irritant smoke. Care shall be taken when performing the

sensitivity screening checks that determine whether the test subject can detect

irritant smoke to use only the minimum amount of smoke necessary to elicit a

response from the test subject.

(5) The fit test shall be performed in an area with adequate ventilation to

prevent exposure of the person conducting the fit test or the build-up of

irritant smoke in the general atmosphere.

(b) Sensitivity Screening Check. The person to be tested must demonstrate his or

her ability to detect a weak concentration of the irritant smoke.

(1) The test operator shall break both ends of a ventilation smoke tube

containing stannic chloride, and attach one end of the smoke tube to a low flow

air pump set to deliver 200 milliliters per minute, or an aspirator squeeze

bulb. The test operator shall cover the other end of the smoke tube with a short

piece of tubing to prevent potential injury from the jagged end of the smoke

tube.

(2) The test operator shall advise the test subject that the smoke can be

irritating to the eyes, lungs, and nasal passages and instruct the subject to

keep his/her eyes closed while the test is performed.

(3) The test subject shall be allowed to smell a weak concentration of the

irritant smoke before the respirator is donned to become familiar with its

irritating properties and to determine if he/she can detect the irritating

properties of the smoke. The test operator shall carefully direct a small amount

of the irritant smoke in the test subject's direction to determine that he/she

can detect it.

(c) Irritant Smoke Fit Test Procedure

(1) The person being fit tested shall don the respirator without assistance, and

perform the required user seal check(s).

(2) The test subject shall be instructed to keep his/her eyes closed.

(3) The test operator shall direct the stream of irritant smoke from the smoke

tube toward the faceseal area of the test subject, using the low flow pump or

the squeeze bulb. The test operator shall begin at least 12 inches from the

facepiece and move the smoke stream around the whole perimeter of the mask. The

operator shall gradually make two more passes around the perimeter of the mask,

moving to within six inches of the respirator.

(4) If the person being tested has not had an involuntary response and/or

detected the irritant smoke, proceed with the test exercises.

(5) The exercises identified in section I.A. 14. of this appendix shall be

performed by the test subject while the respirator seal is being continually

challenged by the smoke, directed around the perimeter of the respirator at a

distance of six inches.

(6) If the person being fit tested reports detecting the irritant smoke at any

time, the test is failed. The person being retested must repeat the entire

sensitivity check and fit test procedure.

(7) Each test subject passing the irritant smoke test without evidence of a

response (involuntary cough, irritation) shall be given a second sensitivity

screening check, with the smoke from the same smoke tube used during the fit

test, once the respirator has been removed, to determine whether he/she still

reacts to the smoke. Failure to evoke a response shall void the fit test.

(8) If a response is produced during this second sensitivity check, then the fit

test is passed.

## C. Quantitative Fit Test (QNFT) Protocols.

The following quantitative fit testing procedures have been demonstrated to be acceptable: Quantitative fit testing using a non-hazardous test aerosol (such as corn oil, polyethylene glycol 400 [PEG 400], di-2-ethyl hexyl sebacate [DEHS], or sodium chloride) generated in a test chamber, and employing instrumentation to quantify the fit

of the respirator; Quantitative fit testing using ambient aerosol as the test

agent and appropriate instrumentation (condensation nuclei counter) to quantify

the respirator fit; Quantitative fit testing using controlled negative pressure

and appropriate instrumentation to measure the volumetric leak rate of a

facepiece to quantify the respirator fit.

1. General

(a) The company shall ensure that persons administering QNFT are able to

calibrate equipment and perform tests properly, recognize invalid tests,

calculate fit factors properly and ensure that test equipment is in proper

working order.

(b) The company shall ensure that QNFT equipment is kept clean, and is

maintained and calibrated according to the manufacturer's instructions so as to

operate at the parameters for which it was designed.

2. Generated Aerosol Quantitative Fit Testing Protocol

(a) Apparatus.

(1) Instrumentation. Aerosol generation, dilution, and measurement systems using

particulates (corn oil, polyethylene glycol 400 [PEG 400], di-2-ethyl hexyl

sebacate [DEHS] or sodium chloride) as test aerosols shall be used for

quantitative fit testing.

(2) Test chamber. The test chamber shall be large enough to permit all test

subjects to perform freely all required exercises without disturbing the test

agent concentration or the measurement apparatus. The test chamber shall be

equipped and constructed so that the test agent is effectively isolated from the

ambient air, yet uniform in concentration throughout the chamber.

(3) When testing air-purifying respirators, the normal filter or cartridge

element shall be replaced with a high efficiency particulate air (HEPA) or P100

series filter supplied by the same manufacturer.

(4) The sampling instrument shall be selected so that a computer record or strip

chart record may be made of the test showing the rise and fall of the test agent

concentration with each inspiration and expiration at fit factors of at least

2,000. Integrators or computers that integrate the amount of test agent

penetration leakage into the respirator for each exercise may be used provided a

record of the readings is made.

(5) The combination of substitute air-purifying elements, test agent and test

agent concentration shall be such that the test subject is not exposed in excess

of an established exposure limit for the test agent at any time during the

testing process, based upon the length of the exposure and the exposure limit

duration.

(6) The sampling port on the test specimen respirator shall be placed and

constructed so that no leakage occurs around the port (e.g., where the

respirator is probed), a free air flow is allowed into the sampling line at all

times, and there is no interference with the fit or performance of the

respirator. The in-mask sampling device (probe) shall be designed and used so

that the air sample is drawn from the breathing zone of the test subject, midway

between the nose and mouth and with the probe extending into the facepiece

cavity at least 1/4 inch.

(7) The test setup shall permit the person administering the test to observe the

test subject inside the chamber during the test.

(8) The equipment generating the test atmosphere shall maintain the

concentration of test agent constant to within a 10 percent variation for the

duration of the test.

(9) The time lag (interval between an event and the recording of the event on

the strip chart or computer or integrator) shall be kept to a minimum. There

shall be a clear association between the occurrence of an event and its being

recorded.

(10) The sampling line tubing for the test chamber atmosphere and for the

respirator sampling port shall be of equal diameter

and of the same material. The length of the two lines shall be equal.

(11) The exhaust flow from the test chamber shall pass through an appropriate

filter (i.e., high efficiency particulate filter) before release.

(12) When sodium chloride aerosol is used, the relative humidity inside the test

chamber shall not exceed 50 percent.

(13) The limitations of instrument detection shall be taken into account when

determining the fit factor.

(14) Test respirators shall be maintained in proper working order and be

inspected regularly for deficiencies such as cracks or missing valves and

gaskets.

(b) Procedural Requirements.

(1) When performing the initial user seal check using a positive or negative

pressure check, the sampling line shall be crimped closed in order to avoid air

pressure leakage during either of these pressure checks.

(2) The use of an abbreviated screening QLFT test is optional. Such a test may

be utilized in order to quickly identify poor fitting respirators that passed

the positive and/or negative pressure test and reduce the amount of QNFT time.

The use of the CNC QNFT instrument in the count mode is another optional method

to obtain a quick estimate of fit and eliminate poor fitting respirators before

going on to perform a full QNFT.

(3) A reasonably stable test agent concentration shall be measured in the test

chamber prior to testing. For canopy or shower curtain types of test units, the

determination of the test agent's stability may be established after the test

subject has entered the test environment.

(4) Immediately after the subject enters the test chamber, the test agent

concentration inside the respirator shall be measured to ensure that the peak

penetration does not exceed 5 percent for a half mask or 1 percent for a full

facepiece respirator.

(5) A stable test agent concentration shall be obtained prior to the actual

start of testing.

(6) Respirator restraining straps shall not be over-tightened for testing. The

straps shall be adjusted by the wearer without assistance from other persons to

give a reasonably comfortable fit typical of normal use. The respirator shall

not be adjusted once the fit test exercises begin.

(7) The test shall be terminated whenever any single peak penetration exceeds 5

percent for half masks and 1 percent for full facepiece respirators. The test

subject shall be refitted and retested.

(8) Calculation of fit factors.

(i) The fit factor shall be determined for the quantitative fit test by taking

the ratio of the average chamber concentration to the concentration measured

inside the respirator for each test exercise except the grimace exercise.

(ii) The average test chamber concentration shall be calculated as the

arithmetic average of the concentration measured before and after each test

(i.e., 7 exercises) or the arithmetic average of the concentration measured

before and after each exercise or the true average measured continuously during

the respirator sample.

(iii) The concentration of the challenge agent inside the respirator shall be

determined by one of the following methods:

(A) Average peak penetration method means the method of determining test agent

penetration into the respirator utilizing a strip chart recorder, integrator, or

computer. The agent penetration is determined by an average of the peak heights

on the graph or by computer integration, for each exercise except the grimace

exercise. Integrators or computers that calculate the actual test agent

penetration into the respirator for each exercise will also be considered to

meet the requirements of the average peak penetration method.

(B) Maximum peak penetration method means the method of determining test agent

penetration in the respirator as determined by strip chart recordings of the

test. The highest peak penetration for a given exercise is taken to be

representative of average penetration into the respirator for that exercise.

(C) Integration by calculation of the area under the individual peak for each

exercise except the grimace exercise. This includes computerized integration.

(D) The calculation of the overall fit factor using individual exercise fit

factors involves first converting the exercise fit factors to penetration

values, determining the average, and then converting that result back to a fit

factor. This procedure is described in the following equation:

Overall Fit Factor = Number of exercises

___________________________________________

1/ff1 + 1/ff2 + 1/ff3 + 1/ff4 + 1/ff5 + 1/ff6 + 1/ff7 + 1/ff8

Where ff1, ff2, ff3, etc. are the fit factors for exercises 1, 2, 3, etc.

(9) The test subject shall not be permitted to wear a half mask or quarter

facepiece respirator unless a minimum fit factor of 100 is obtained, or a full

facepiece respirator unless a minimum fit factor of 500 is obtained.

(10) Filters used for quantitative fit testing shall be replaced whenever

increased breathing resistance is encountered, or when the test agent has

altered the integrity of the filter media.

3. Ambient aerosol condensation nuclei counter (CNC) quantitative fit testing

protocol. The ambient aerosol condensation nuclei counter (CNC) quantitative fit

testing (Portacount TM) protocol quantitatively fit tests respirators with the

use of a probe. The probed respirator is only used for quantitative fit tests. A

probed respirator has a special sampling device, installed on the respirator,

that allows the probe to sample the air from inside the mask. A probed

respirator is required for each make, style, model, and size that the company

uses and can be obtained from the respirator manufacturer or distributor. The

CNC instrument manufacturer, TSI Inc., also provides probe attachments (TSI

sampling adapters) that permit fit testing in an employee's own respirator. A

minimum fit factor pass level of at least 100 is necessary for a half-mask

respirator and a minimum fit factor pass level of at least 500 is required for a

full facepiece negative pressure respirator. The entire screening and testing

procedure shall be explained to the test subject prior to the conduct of the

screening test.

(a) Portacount Fit Test Requirements.

(1) Check the respirator to make sure the sampling probe and line are properly

attached to the facepiece and that the respirator is fitted with a particulate

filter capable of preventing significant penetration by the ambient particles

used by the fit test (e.g. NIOSH 42 CFR 84 series 100, 99 or 95 particulate

filter) per manufacturer’s instruction.

(2) Instruct the person to be tested to don the respirator for five minutes

before the fit test starts. This purges the ambient particles trapped inside the

respirator and permits the wearer to make certain the respirator is comfortable.

This individual shall already have been trained on how to wear the respirator

properly.

(3) Check the following conditions for the adequacy of the respirator fit: Chin

properly placed; Adequate strap tension, not overly tightened; Fit across nose

bridge; Respirator of proper size to span distance from nose to chin; Tendency

of the respirator to slip; Self-observation in a mirror to evaluate fit and

respirator position.

(4) Have the person wearing the respirator do a user seal check. If leakage is

detected, determine the cause. If leakage is from a poorly fitting facepiece,

try another size of the same model respirator, or another model of respirator.

(5) Follow the manufacturer's instructions for operating the Portacount and

proceed with the test.

(6) The test subject shall be instructed to perform the exercises in section I.

A. 14. of this appendix.

(7) After the test exercises, the test subject shall be questioned by the test

conductor regarding the comfort of the respirator upon completion of the

protocol. If it has become unacceptable, another model of respirator shall be

tried.

(b) Portacount Test Instrument.

(1) The Portacount will automatically stop and calculate the overall fit factor

for the entire set of exercises. The overall fit factor is what counts. The Pass

or Fail message will indicate whether or not the test was successful. If the

test was a Pass, the fit test is over.

(2) Since the pass or fail criterion of the Portacount is user programmable, the

test operator shall ensure that the pass or fail criterion meet the requirements

for minimum respirator performance in this Appendix.

(3) A record of the test needs to be kept on file, assuming the fit test was

successful. The record must contain the test subject's name; overall fit factor;

make, model, style, and size of respirator used; and date tested.

4. Controlled negative pressure (CNP) quantitative fit testing protocol. The CNP

protocol provides an alternative to aerosol fit test methods. The CNP fit test

method technology is based on exhausting air from a temporarily sealed

respirator facepiece to generate and then maintain a constant negative pressure

inside the facepiece. The rate of air exhaust is controlled so that a constant

negative pressure is maintained in the respirator during the fit test. The level

of pressure is selected to replicate the mean inspiratory pressure that causes

leakage into the respirator under normal use conditions. With pressure held

constant, air flow out of the respirator is equal to air flow into the

respirator. Therefore, measurement of the exhaust stream that is required to

hold the pressure in the temporarily sealed respirator constant yields a direct

measure of leakage air flow into the respirator. The CNP fit test method

measures leak rates through the facepiece as a method for determining the

facepiece fit for negative pressure respirators. The CNP instrument manufacturer

Dynatech Nevada also provides attachments (sampling manifolds) that replace the filter cartridges to permit fit testing in an employee's own respirator. To

perform the test, the test subject closes his or her mouth and holds his/her

breath, after which an air pump removes air from the respirator facepiece at a

pre-selected constant pressure. The facepiece fit is expressed as the leak rate

through the facepiece, expressed as milliliters per minute. The quality and

validity of the CNP fit tests are determined by the degree to which the in-mask

pressure tracks the test pressure during the system measurement time of

approximately five seconds. Instantaneous feedback in the form of a real-time

pressure trace of the in-mask pressure is provided and used to determine test

validity and quality. A minimum fit factor pass level of 100 is necessary for a

half-mask respirator and a minimum fit factor of at least 500 is required for a

full facepiece respirator. The entire screening and testing procedure

shall be explained to the test subject prior to the conduct of the screening

test.

(a) CNP Fit Test Requirements.

(1) The instrument shall have a non-adjustable test pressure of 15.0 mm water

pressure.

(2) The CNP system defaults selected for test pressure shall be set at -15 mm of

water (-0.58 inches of water) and the modeled inspiratory flow rate shall be

53.8 liters per minute for performing fit tests.

(Note: CNP systems have built-in capability to conduct fit testing that is

specific to unique work rate, mask, and gender situations that might apply in a

specific workplace. Use of system default values, which were selected to

represent respirator wear with medium cartridge resistance at a low-moderate

work rate, will allow inter-test comparison of the respirator fit.)

(3) The individual who conducts the CNP fit testing shall be thoroughly trained

to perform the test.

(4) The respirator filter or cartridge needs to be replaced with the CNP test

manifold. The inhalation valve downstream from the manifold either needs to be

temporarily removed or propped open.

(5) The test subject shall be trained to hold his or her breath for at least 20

seconds.

(6) The test subject shall don the test respirator without any assistance from

the individual who conducts the CNP fit test.

(7) The QNFT protocol shall be followed according to section I. C. 1. of this

appendix with an exception for the CNP test exercises.

(b) CNP Test Exercises.

(1) Normal breathing. In a normal standing position, without talking, the

subject shall breathe normally for 1 minute. After the normal breathing

exercise, the subject needs to hold head straight ahead and hold his or her

breath for 10 seconds during the test measurement.

(2) Deep breathing. In a normal standing position, the subject shall breathe

slowly and deeply for 1 minute, being careful not to hyperventilate. After the

deep breathing exercise, the subject shall hold his or her head straight ahead

and hold his or her breath for 10 seconds during test measurement.

(3) Turning head side to side. Standing in place, the subject shall slowly turn

his or her head from side to side between the extreme positions on each side for

1 minute. The head shall be held at each extreme momentarily so the subject can inhale at each side. After the turning head side to side exercise, the subject

needs to hold head full left and hold his or her breath for 10 seconds during

test measurement. Next, the subject needs to hold head full right and hold his

or her breath for 10 seconds during test measurement.

(4) Moving head up and down. Standing in place, the subject shall slowly move

his or her head up and down for 1 minute. The subject shall be instructed to

inhale in the up position (i.e., when looking toward the ceiling). After the

moving head up and down exercise, the subject shall hold his or her head full up

and hold his or her breath for 10 seconds during test measurement. Next, the

subject shall hold his or her head full down and hold his or her breath for 10

seconds during test measurement.

(5) Talking. The subject shall talk out loud slowly and loud enough so as to be

heard clearly by the test conductor. The subject can read from a prepared text

such as the Rainbow Passage, count backward from 100, or recite a memorized poem or song for 1 minute. After the talking exercise, the subject shall hold his or

her head straight ahead and hold his or her breath for 10 seconds during the

test measurement.

(6) Grimace. The test subject shall grimace by smiling or frowning for 15

seconds.

(7) Bending Over. The test subject shall bend at the waist as if he or she were

to touch his or her toes for 1 minute. Jogging in place shall be substituted for

this exercise in those test environments such as shroud-type QNFT units that

prohibit bending at the waist. After the bending over exercise, the subject

shall hold his or her head straight ahead and hold his or her breath for 10

seconds during the test measurement.

(8) Normal Breathing. The test subject shall remove and re-don the respirator

within a one-minute period. Then, in a normal standing position, without

talking, the subject shall breathe normally for 1 minute. After the normal

breathing exercise, the subject shall hold his or her head straight ahead and

hold his or her breath for 10 seconds during the test measurement. After the

test exercises, the test subject shall be questioned by the test conductor

regarding the comfort of the respirator upon completion of the protocol. If it

has become unacceptable, another model of a respirator shall be tried.

(c) CNP Test Instrument.

(1) The test instrument shall have an effective audio warning device when the

test subject fails to hold his or her breath during the test. The test shall be

terminated whenever the test subject failed to hold his or her breath. The test

subject may be refitted and retested.

(2) A record of the test shall be kept on file, assuming the fit test was

successful. The record must contain the test subject's name; overall fit factor;

make, model, style and size of respirator used; and date tested.

Part II. New Fit Test Protocols

A. Any person may submit to OSHA an application for approval of a new fit test

protocol. If the application meets the following criteria, OSHA will initiate a

rulemaking proceeding under section 6(b) (7) of the OSH Act to determine whether

to list the new protocol as an approved protocol in this Appendix A.

B. The application must include a detailed description of the proposed new fit

test protocol. This application must be supported by either:

1. A test report prepared by an independent government research laboratory

(e.g., Lawrence Livermore National Laboratory, Los Alamos National Laboratory,

the National Institute for Standards and Technology) stating that the laboratory

has tested the protocol and had found it to be accurate and reliable; or

2. An article that has been published in a peer-reviewed industrial hygiene

journal describing the protocol and explaining how test data support the

protocol's accuracy and reliability.

C. If OSHA determines that additional information is required before the Agency

commences a rulemaking proceeding under this section, OSHA will so notify the

applicant and afford the applicant the opportunity to submit the supplemental

information. Initiation of a rulemaking proceeding will be deferred until OSHA

has received and evaluated the supplemental information.

## Appendix B-1: User Seal Check Procedures (Mandatory)

The individual who uses a tight-fitting respirator is to perform a user seal

check to ensure that an adequate seal is achieved each time the respirator is

put on. Either the positive and negative pressure checks listed in this

appendix or the respirator manufacturer's recommended user seal check method

shall be used. User seal checks are not substitutes for qualitative or

quantitative fit tests.

I. Facepiece Positive and/or Negative Pressure Checks.

A. Positive pressure check. Close off the exhalation valve and exhale gently

into the facepiece. The face fit is considered satisfactory if a slight positive

pressure can be built up inside the facepiece without any evidence of outward

leakage of air at the seal. For most respirators this method of leak testing

requires the wearer to first remove the exhalation valve cover before closing

off the exhalation valve and then carefully replacing it after the test.

B. Negative pressure check. Close off the inlet opening of the canister or

cartridge(s) by covering with the palm of the hand(s) or by replacing the filter

seal(s), inhale gently so that the facepiece collapses slightly, and hold the

breath for ten seconds. The design of the inlet opening of some cartridges

cannot be effectively covered with the palm of the hand. The test can be

performed by covering the inlet opening of the cartridge with a thin latex or

nitrile glove. If the facepiece remains in its slightly collapsed condition and

no inward leakage of air is detected, the tightness of the respirator is

considered satisfactory.

II. Manufacturer's Recommended User Seal Check Procedures. The respirator

manufacturer's recommended procedures for performing a user seal check may be used instead of the positive and/or negative pressure check procedures provided that the company demonstrates that the manufacturer's procedures are equally effective.

## Appendix B-2: Respirator Cleaning Procedures (Mandatory)

These procedures are provided for company use when cleaning respirators. They are general in nature, and the company as an alternative may use the cleaning recommendations provided by the manufacturer of the respirators used by their employees, provided such procedures are as effective as those listed here in Appendix B-2. Equivalent effectiveness simply means that the procedures used must accomplish the objectives set forth in Appendix B-2, i.e., must ensure that the respirator is properly cleaned and disinfected in a manner that prevents

damage to the respirator and does not cause harm to the user.

I. Procedures for Cleaning Respirators.

A. Remove filters, cartridges, or canisters. Disassemble facepieces by removing

speaking diaphragms, demand and pressure-demand valve assemblies, hoses, or any components recommended by the manufacturer. Discard or repair any defective parts.

B. Wash components in warm (43 deg. C [110 deg. F] maximum) water with a mild detergent or with a cleaner recommended by the manufacturer. A stiff bristle

(not wire) brush may be used to facilitate the removal of dirt.

C. Rinse components thoroughly in clean, warm (43 deg. C [110 deg. F] maximum), preferably running water. Drain.

D. When the cleaner used does not contain a disinfecting agent, respirator

components should be immersed for two minutes in one of the following:

1. Hypochlorite solution (50 ppm of chlorine) made by adding approximately one

milliliter of laundry bleach to one liter of water at 43 deg. C (110 deg. F);

or,

2. Aqueous solution of iodine (50 ppm iodine) made by adding approximately 0.8

milliliters of tincture of iodine (6-8 grams ammonium and/or potassium

iodide/100 cc of 45% alcohol) to one liter of water at 43 deg. C (110 deg. F);

or,

3. Other commercially available cleansers of equivalent disinfectant quality

when used as directed, if their use is recommended or approved by the respirator

manufacturer.

E. Rinse components thoroughly in clean, warm (43 deg. C [110 deg. F] maximum),

preferably running water. Drain. The importance of thorough rinsing cannot be

overemphasized. Detergents or disinfectants that dry on facepieces may result in

dermatitis. In addition, some disinfectants may cause deterioration of rubber or

corrosion of metal parts if not completely removed.

F. Components should be hand-dried with a clean lint-free cloth or air-dried.

G. Reassemble facepiece, replacing filters, cartridges, and canisters where

necessary.

H. Test the respirator to ensure that all components work properly.

## Appendix C: OSHA Respirator Medical Evaluation Questionnaire (Mandatory)

To the company: Answers to questions in Section 1, and to question 9 in Section

2 of Part A do not require a medical examination.

To the employee:

Can you read (circle one): Yes/No

Your company must allow you to answer this questionnaire during normal working hours, or at a time and place that is convenient to you. To maintain your

confidentiality, your company or supervisor must not look at or review your

answers and your company must tell you how to deliver or send this

questionnaire to the health care professional who will review it.

Part A. Section 1. (Mandatory) The following information must be provided by

every employee who has been selected to use any type of respirator (please print).

1. Today's date:-------------------------------------------------------

2. Your name:----------------------------------------------------------

3. Your age (to nearest year):-----------------------------------------

4. Sex (circle one): Male/Female

5. Your height: __________ ft. __________ in.

6. Your weight: ____________ lbs.

7. Your job title:-----------------------------------------------------

8. A phone number where you can be reached by the health care professional who reviews this questionnaire (include the Area Code):

9. The best time to phone you at this number:

10. Has your company told you how to contact the health care professional who

will review this questionnaire (circle one): Yes/No

11. Check the type of respirator you will use (you can check more than one

category):

a.  N, R, or P disposable respirator (filter-mask, non-cartridge type only).

b. Other type (for example, half- or full-facepiece type, powered-air purifying,

supplied-air, self-contained breathing apparatus).

12. Have you worn a respirator (circle one): Yes/No

If "yes," what type(s):

Part A. Section 2. (Mandatory) Questions 1 through 9 below must be answered by every employee who has been selected to use any type of respirator (please circle "yes" or "no").

1. Do you currently smoke tobacco, or have you smoked tobacco in the last month:

Yes/No

2. Have you ever had any of the following conditions?

a. Seizures (fits): Yes/No

b. Diabetes (sugar disease): Yes/No

c. Allergic reactions that interfere with your breathing: Yes/No

d. Claustrophobia (fear of closed-in places): Yes/No

e. Trouble smelling odors: Yes/No

3. Have you ever had any of the following pulmonary or lung problems?

a. Asbestosis: Yes/No

b. Asthma: Yes/No

c. Chronic bronchitis: Yes/No

d. Emphysema: Yes/No

e. Pneumonia: Yes/No

f. Tuberculosis: Yes/No

g. Silicosis: Yes/No

h. Pneumothorax (collapsed lung): Yes/No

i. Lung cancer: Yes/No

j. Broken ribs: Yes/No

k. Any chest injuries or surgeries: Yes/No

l. Any other lung problem that you've been told about: Yes/No

4. Do you currently have any of the following symptoms of pulmonary or lung

illness?

a. Shortness of breath: Yes/No

b. Shortness of breath when walking fast on level ground or walking up a slight

hill or incline: Yes/No

c. Shortness of breath when walking with other people at an ordinary pace on

level ground: Yes/No

d. Have to stop for breath when walking at your own pace on level ground: Yes/No

e. Shortness of breath when washing or dressing yourself: Yes/No

f. Shortness of breath that interferes with your job: Yes/No

g. Coughing that produces phlegm (thick sputum): Yes/No

h. Coughing that wakes you early in the morning: Yes/No

i. Coughing that occurs mostly when you are lying down: Yes/No

j. Coughing up blood in the last month: Yes/No

k. Wheezing: Yes/No

l. Wheezing that interferes with your job: Yes/No

m. Chest pain when you breathe deeply: Yes/No

n. Any other symptoms that you think may be related to lung problems: Yes/No

5. Have you ever had any of the following cardiovascular or heart problems?

a. Heart attack: Yes/No

b. Stroke: Yes/No

c. Angina: Yes/No

d. Heart failure: Yes/No

e. Swelling in your legs or feet (not caused by walking): Yes/No

f. Heart arrhythmia (heart beating irregularly): Yes/No

g. High blood pressure: Yes/No

h. Any other heart problem that you've been told about: Yes/No

6. Have you ever had any of the following cardiovascular or heart symptoms?

a. Frequent pain or tightness in your chest: Yes/No

b. Pain or tightness in your chest during physical activity: Yes/No

c. Pain or tightness in your chest that interferes with your job: Yes/No

d. In the past two years, have you noticed your heart skipping or missing a

beat: Yes/No

e. Heartburn or indigestion that is not related to eating: Yes/No

f. Any other symptoms that you think may be related to heart or circulation

problems: Yes/No

7. Do you currently take medication for any of the following problems?

a. Breathing or lung problems: Yes/No

b. Heart trouble: Yes/No

c. Blood pressure: Yes/No

d. Seizures (fits): Yes/No

8. If you've used a respirator, have you ever had any of the following problems?

(If you've never used a respirator, check the following space and go to question

9:)

a. Eye irritation: Yes/No

b. Skin allergies or rashes: Yes/No

c. Anxiety: Yes/No

d. General weakness or fatigue: Yes/No

e. Any other problem that interferes with your use of a respirator: Yes/No

9. Would you like to talk to the health care professional who will review this

questionnaire about your answers to this questionnaire: Yes/No

Questions 10 to 15 below must be answered by every employee who has been

selected to use either a full-facepiece respirator or a self-contained breathing

apparatus (SCBA). For employees who have been selected to use other types of

respirators, answering these questions is voluntary.

10. Have you ever lost vision in either eye (temporarily or permanently): Yes/No

11. Do you currently have any of the following vision problems?

a. Wear contact lenses: Yes/No

b. Wear glasses: Yes/No

c. Color blind: Yes/No

d. Any other eye or vision problem: Yes/No

12. Have you ever had an injury to your ears, including a broken ear drum:

Yes/No

13. Do you currently have any of the following hearing problems?

a. Difficulty hearing: Yes/No

b. Wear a hearing aid: Yes/No

c. Any other hearing or ear problem: Yes/No

14. Have you ever had a back injury: Yes/No

15. Do you currently have any of the following musculoskeletal problems?

a. Weakness in any of your arms, hands, legs, or feet: Yes/No

b. Back pain: Yes/No

c. Difficulty fully moving your arms and legs: Yes/No

d. Pain or stiffness when you lean forward or backward at the waist: Yes/No

e. Difficulty fully moving your head up or down: Yes/No

f. Difficulty fully moving your head side to side: Yes/No

g. Difficulty bending at your knees: Yes/No

h. Difficulty squatting to the ground: Yes/No

i. Climbing a flight of stairs or a ladder carrying more than 25 lbs: Yes/No

j. Any other muscle or skeletal problem that interferes with using a respirator:

Yes/No

Part B.

Any of the following questions, and other questions not listed, may be

added to the questionnaire at the discretion of the health care professional who

will review the questionnaire.

1. In your present job, are you working at high altitudes (over 5,000 feet) or

in a place that has lower than normal amounts of oxygen: Yes/No

If "yes," do you have feelings of dizziness, shortness of breath, pounding in

your chest, or other symptoms when you're working under these conditions: Yes/No

2. At work or at home, have you ever been exposed to hazardous solvents,

hazardous airborne chemicals (e.g., gases, fumes, or dust), or have you come

into skin contact with hazardous chemicals: Yes/No

If "yes," name the chemicals if you know them:

3. Have you ever worked with any of the materials, or under any of the

conditions, listed below:

a. Asbestos: Yes/No

b. Silica (e.g., in sandblasting): Yes/No

c. Tungsten/cobalt (e.g., grinding or welding this material): Yes/No

d. Beryllium: Yes/No

e. Aluminum: Yes/No

f. Coal (for example, mining): Yes/No

g. Iron: Yes/No

h. Tin: Yes/No

i. Dusty environments: Yes/No

j. Any other hazardous exposures: Yes/No

If "yes," describe these exposures:

4. List any second jobs or side businesses you have:

5. List your previous occupations:

6. List your current and previous hobbies:

7. Have you been in the military services? Yes/No

If "yes," were you exposed to biological or chemical agents (either in training

or combat): Yes/No

8. Have you ever worked on a HAZMAT team? Yes/No

9. Other than medications for breathing and lung problems, heart trouble, blood

pressure, and seizures mentioned earlier in this questionnaire, are you taking

any other medications for any reason (including over-the-counter medications):

Yes/No

If "yes," name the medications if you know them:

10. Will you be using any of the following items with your respirator(s)?

a. HEPA Filters: Yes/No

b. Canisters (for example, gas masks): Yes/No

c. Cartridges: Yes/No

11. How often are you expected to use the respirator(s) (circle "yes" or "no"

for all answers that apply to you)?:

a. Escape only (no rescue): Yes/No

b. Emergency rescue only: Yes/No

c. Less than 5 hours per week: Yes/No

d. Less than 2 hours per day: Yes/No

e. 2 to 4 hours per day: Yes/No

f. Over 4 hours per day: Yes/No

12. During the period you are using the respirator(s), is your work effort:

a. Light (less than 200 kcal per hour): Yes/No

If "yes," how long does this period last during the average

shift:____________hrs.____________mins.

Examples of a light work effort are sitting while writing, typing, drafting, or

performing light assembly work; or standing while operating a drill press (1-3

lbs.) or controlling machines.

b. Moderate (200 to 350 kcal per hour): Yes/No

If "yes," how long does this period last during the average

shift:____________hrs.____________mins.

Examples of moderate work effort are sitting while nailing or filing; driving a

truck or bus in urban traffic; standing while drilling, nailing, performing

assembly work, or transferring a moderate load (about 35 lbs.) at trunk level;

walking on a level surface about 2 mph or down a 5-degree grade about 3 mph; or

pushing a wheelbarrow with a heavy load (about 100 lbs.) on a level surface.

c. Heavy (above 350 kcal per hour): Yes/No

If "yes," how long does this period last during the average

shift:____________hrs.____________mins.

Examples of heavy work are lifting a heavy load (about 50 lbs.) from the floor

to your waist or shoulder; working on a loading dock; shoveling; standing while

bricklaying or chipping castings; walking up an 8-degree grade about 2 mph;

climbing stairs with a heavy load (about 50 lbs.).

13. Will you be wearing protective clothing and/or equipment (other than the

respirator) when you're using your respirator: Yes/No

If "yes," describe this protective clothing and/or equipment:

14. Will you be working under hot conditions (temperature exceeding 77 deg. F): Yes/No

15. Will you be working under humid conditions: Yes/No

16. Describe the work you'll be doing while you're using your respirator(s):

17. Describe any special or hazardous conditions you might encounter when you're

using your respirator(s) (for example, confined spaces, life-threatening gases):

18. Provide the following information, if you know it, for each toxic substance

that you'll be exposed to when you're using your respirator(s):

Name of the first toxic substance:

Estimated maximum exposure level per shift:

Duration of exposure per shift

Name of the second toxic substance:

Estimated maximum exposure level per shift:

Duration of exposure per shift:

Name of the third toxic substance:

Estimated maximum exposure level per shift:

Duration of exposure per shift:

The name of any other toxic substances that you'll be exposed to while using

your respirator:

19. Describe any special responsibilities you'll have while using your

respirator(s) that may affect the safety and well-being of others (for example,

rescue, security):

## Appendix D (Mandatory)

## Information for Employees Using Respirators When Not Required Under the Standard.

Respirators are an effective method of protection against designated hazards

when properly selected and worn. Respirator use is encouraged, even when

exposures are below the exposure limit, to provide an additional level of

comfort and protection for workers. However, if a respirator is used improperly

or not kept clean, the respirator itself can become a hazard to the worker.

Sometimes, workers may wear respirators to avoid exposures to hazards, even if

the amount of hazardous substance does not exceed the limits set by OSHA

standards. If your company provides respirators for your voluntary use, or if

you provide your own respirator, you need to take certain precautions to be sure

that the respirator itself does not present a hazard.

You should do the following:

1. Read and heed all instructions provided by the manufacturer on use,

maintenance, cleaning and care, and warnings regarding the respirators

limitations.

2. Choose respirators certified for use to protect against the contaminant of

concern. NIOSH, the National Institute for Occupational Safety and Health of the

U.S. Department of Health and Human Services, certifies respirators. A label or

statement of certification should appear on the respirator or respirator

packaging. It will tell you what the respirator is designed for and how much it

will protect you.

3. Do not wear your respirator into atmospheres containing contaminants for

which your respirator is not designed to protect against. For example, a

respirator designed to filter dust particles will not protect you against gases,

vapors, or very small solid particles of fumes or smoke.

4. Keep track of your respirator so that you do not mistakenly use someone

else's respirator.

## Ventilation and Personal Protective Equipment Requirements for Spray Coating Operations.

(a) General. Spray coating operations whenever practicable shall be confined to

properly designed, constructed and adequately ventilated spray booths or spray

rooms which meet all the requirements of both this section and Article 137.

(b) Operation.

(1) Mechanical ventilation shall be kept in operation at all times while

spraying operations are being conducted and for a sufficient time thereafter to

allow flammable vapors from drying coated articles and drying finishing material

residue to be exhausted.

(2) When spray is automatically applied without an attendant constantly on duty,

the operating control of spray apparatus shall be so arranged that spray cannot

be applied unless exhaust fans are in operation.

(c) Exhaust and Make-Up Air.

(1) Air exhausted from spray operations shall not be recirculated. Safe

arrangements should be provided for an adequate supply of make-up air to

compensate for air exhausted from spraying operations.

(2) No means of heating make-up air shall be located in a spray booth.

(d) Dilution of Flammable Vapors. Ventilation in spray facilities shall be

sufficient to dilute flammable vapors to less than 20 percent of their lower

explosive limit as specified in Section 5416. Lower explosive limits of common

solvents are listed in NFPA No. 49-1973, Hazardous Chemicals Data.

(e) Ventilation Rates. The velocity of air into all openings of a spray booth

shall be not less than that specified in Table V-6.

TABLE V-6

MINIMUM MAINTAINED VELOCITIES INTO SPRAY BOOTHS

Operating Conditions for

Objects Completely Inside    Crossdraft,     Airflow Velocities,       f.p.m.

Booth                                     f.p.m.               Average              Minimum

Electrostatic and automatic

airless operation..........          Up to 50        60 large booth             60

100 small booth         75

Air-operated guns, manual

or automatic...............           Up to 50        100 large booth         75

150 small booth        125

Air-operated guns, manual

or automatic...............     From 50 to 100    150 large booth      125

200 small booth      150

NOTE: A large booth is a walk-in size booth.

(f) Downdraft Booths.

Where downdraft booths are provided with doors, such doors shall be closed when spray painting.

(g) Respiratory Protection.

A spray booth operator is required to wear a respirator when he is positioned

downstream from the object being sprayed. Respirator use shall conform to the

requirements.

## Retention of DOT Markings, Placards and Labels.

(a) Any company who receives a package of hazardous material which is required to be marked, labeled or placarded in accordance with the U.S. Department of Transportation's Hazardous Materials Regulations (49 CFR Parts 171 through 180) shall retain those markings, labels and placards on the package until the packaging is sufficiently cleaned of residue and purged of vapors to remove any potential hazards.

(b) Any company who received a freight container, rail freight car, motor

vehicle, or transport vehicle that is required to be marked or placarded in

accordance with the Hazardous Materials Regulations shall retain those markings and placards on the freight container, rail freight car, motor vehicle or

transport vehicle until the hazardous materials which require the marking or

placarding are sufficiently removed to prevent any potential hazards.

(c) Markings, placards and labels shall be maintained in a manner that ensures

that they are readily visible.

(d) For non-bulk packages which will not be reshipped, the provisions of this

section are met if a label or other acceptable marking is affixed in accordance

with the Hazard Communications Standard.

(e) For the purposes of this section the term "hazardous material" and any other

terms not defined in this section have the same definition as in the Hazardous

Materials Regulations (49 CFR Parts 171 through 180).

## Scope for Spray Coating Operations.

(a) Scope. This Article covers the application of flammable or combustible

materials when applied as a spray by compressed air, "airless" or "hydraulic

atomization," or by steam, or electrostatic methods or by any other means in

continuous or intermittent processes. It also covers the application of

combustible powders when applied by powder spray guns, electrostatic powder

spray guns, fluidized beds or electrostatic fluidized beds.

NOTE: This Article does not cover outdoor spray application of buildings, tanks

or other similar structures, nor small portable spraying apparatus not used

repeatedly in the same location; however, the safeguards contained in this

Article pertaining to cleanliness, care of flammable liquids, dangerous

vapor-air or powder-air mixtures and sources of ignition should be followed

where applicable.

(b) This Article does not cover the spray application of noncombustible

finishing material. Certain water type finishes, however, although involving

little or no hazard in the liquid state may leave highly combustible residues

upon evaporation of the liquid carrier. The provisions of this standard for

minimizing the hazards of combustible residues shall be followed irrespective of

the characteristics of the liquid.

(c) Spray rooms shall meet the requirements of outlined in the following 5 sections.

## Spray Booths.

(a) Spray booths and connected ductwork shall be substantially constructed of

steel, securely and rigidly supported, or of concrete or masonry, except that

aluminum or other substantial noncombustible material may be used for

intermittent or low volume spraying. Spray booths shall be designed to sweep or

guide air currents toward the exhaust outlet.

(b) The interior surfaces of spray booths shall be smooth and continuous without

edges and otherwise designed to prevent pocketing of residues and facilitate

cleaning and washing without injury.

(c) The floor surface of a spray booth and operator's working area, if

combustible, shall be covered with noncombustible material of such character as

to facilitate the safe cleaning and removal of residues.

(d) Distribution or baffle plates, if installed to promote an even flow of air

through booth or cause the deposit of overspray before it enters exhaust duct,

shall be of noncombustible material and readily removable or accessible on both

sides for cleaning. Such plates shall not be located in exhaust ducts.

(e) Every spray booth having an open front elevation larger in area than 9

square feet and which is not equipped with doors, shall have a fire curtain or

metal deflector not less than 2 1/2 inches deep installed at the upper outer

edge of the booth opening.

(f) Where conveyors are arranged to carry work into or out of spray booths, the

openings therefore shall be as small as practical.

(g) Each spray booth shall be separated from other dissimilar operations by not

less than three feet, or by a greater distance, or by such partition or wall as

to reduce the danger from adjacent hazardous operations.

(h) Spray booths shall be so installed that all portions are readily accessible

for cleaning. A clear space of not less than three feet on all sides shall be

kept free from storage or combustible construction.

NOTE: This does not preclude the installation of a spray booth against a

partition or wall having a one hour fire resistance rating providing the booth

can be maintained and cleaned.

## Dry Type Overspray Collectors (Exhaust Air Filters).

(a) In conventional dry type spray booths, overspray dry filters or filter

rolls, if installed, shall conform to the following:

(1) Visible gauges or audible alarms or pressure activated devices shall be

installed to indicate or insure that the required air velocity is

maintained.(See Section 5153). Dry spray booth equipped with a filter roll which

is automatically advanced when the air velocity is reduced to that specified in

this Section shall be arranged to cause shutdown of spraying operations if the

filter roll fails to advance automatically.

(2) Maintenance procedures shall be established to assure replacing filter pads

before excessive restriction to air flow occurs. Filter pads shall be inspected

after each period of use and clogged filter pads discarded and replaced. Filter

rolls shall be inspected to insure proper replacement of filter media.

(3) All discarded filter pads and filter rolls shall be immediately removed to a

safe, well detached location or placed in a water-filled metal container and

disposed of at the close of the day's operation unless maintained completely in

water.

(4) The location of filters in a spray booth shall not reduce the effective

booth enclosure of the articles being sprayed.

(5) Space within spray booth on the downstream and upstream sides of filters

shall be protected with approved automatic sprinklers.

(6) Filters or filter rolls shall not be used when applying a spray material

known to be highly susceptible to spontaneous heating and ignition.

(7) Those parts of the booth which act as supports for, or holders of filters or

filter rolls shall be noncombustible.

(8) Clean filters or filter rolls shall be noncombustible or of a type having a

combustibility not in excess of Class 2 filters as listed by Underwriters'

Laboratories, Inc.

(9) Filters and filter rolls shall not be alternately used for different types

of coating materials, where the combination of materials may be conducive to

spontaneous ignition. See also Section 5453(l).

## Washing Chamber.

(a) For wet or water wash spray booths, the water chamber enclosure, within which intimate contact of contaminated air and cleaning water or other cleaning medium is maintained, if made of steel, shall be 18 gage or heavier and adequately protected against corrosion.

(b) Chambers shall be provided with adequate means for creating and maintaining scrubbing action for removal of particulate matter from the exhaust air stream.

(c) Collecting tanks shall be of welded steel construction or other suitable noncombustible material. If pits are used as collecting tanks, they shall be concrete, masonry, or other material having similar properties.

(d) Tanks shall be provided with weirs, skimmer plates, or screens to prevent sludge and floating paint from entering the pump suction box. Means for automatically maintaining the proper water level shall also be provided. Fresh water inlets shall not be submerged. They shall terminate at least one pipe diameter above the safety overflow level of the tank.

(e) Tanks shall be so constructed as to prevent excessive accumulation of hazardous deposits.

(f) Pump manifolds, risers, and headers shall be adequately sized to ensure sufficient water flow to provide efficient operation of the water chamber.

NOTE: Cleanout means should be provided to permit mechanical cleaning of headers.

## Electrical and Other Sources of Ignition.

All electrical equipment, open flames and other sources of ignition shall

conform to the requirements of this Section, except as follows:

Electrostatic apparatus shall conform to the requirements of Sections of Electrostatic Hand Spraying Equipment and Drying, Curing or Fusion Apparatus.

Finishing operations as described in Subsection (m).

There shall be no open flame, spark producing equipment or exposed surfaces exceeding the ignition temperature of the material being sprayed in any spraying area nor within 20 feet thereof, unless separated by a partition.

Space heating appliances, steam pipes or hot surfaces shall not be located in a spraying area where deposits of combustible residues may readily accumulate and be ignited.

Electrical wiring and equipment shall conform to the provisions of this Section and shall otherwise be in accordance with the [State] Electrical Safety Orders.

Unless specifically approved for locations containing both deposits of readily ignitable residue and explosive vapors, there shall be no electrical equipment in any spraying area, where on deposits of combustible residues may readily accumulate, except wiring in rigid metal conduit, Type MI cable, or in metal boxes or fittings containing no taps, splices or terminal connections.

Electrical wiring and equipment not subject to deposits of combustible residues but located in a spraying area shall be of explosion-proof or other type approved for Class I, Division 1, Group D locations and shall otherwise conform to the provisions of the Electrical Safety Orders for Class I, Division 1 locations.

Equipment within twenty feet horizontally and ten feet vertically, of any spraying operation and not enclosed in a spray booth, shall not produce sparks under normal operating conditions, and shall otherwise conform to the provisions of the Electrical Safety Orders for Class I, Division 2, locations. See Figure SB-1.

Figure SB-1

When spraying areas are illuminated through glass panels or other transparent materials, only fixed lighting units shall be used as a source of illumination. Panels shall isolate the spraying area from the area in which the lighting unit is located, and shall be of a noncombustible material of such a nature or so protected that breakage will be unlikely. Panels shall be so arranged that normal accumulations of residue on the exposed surface of the panel will not be raised to a dangerous temperature to cause vapors and/or ignition by radiation or conduction from the source of illumination.

Electric lamps outside of, but within twenty feet of any spraying area and not separated by a partition, shall be totally enclosed to prevent the falling of hot particles and shall be protected from mechanical injury by guards or by location.

Portable electric lamps shall not be used in any spraying area during spraying operations. Portable electric lamps, if used during cleaning or repairing operations, shall be of the type approved for Class I, Group D, Division 1 locations.

All metal parts of spray booths, exhaust ducts and piping systems conveying flammable or combustible liquids or aerated solids shall be electrically grounded in an effective and permanent manner.

Airless high fluid pressure spray guns and any conductive object being sprayed shall be electrically grounded.

EXCEPTION: Equipment specifically intended to be operated at other than ground potential.

Where the product to be sprayed is brought into a spraying area, removed from it, or manipulated while there, by a self-powered vehicle capable of producing ignition, the vehicle shall not be activated while in the area unless the spraying operation is stopped, the ventilation system is in operation and the area has been purged of vapors to ensure a nonflammable atmosphere.

## Ventilation.

(a) Ventilation requirements shall conform to the provisions of Section of Operation and Maintenance and General Requirements of Mechanical Ventilation Systems and this Section.

(b) Except as permitted in Section of Powder Coating, each spray booth shall have an independent exhaust duct system discharging to the building exterior. Multiple cabinet spray booths in which identical spray finishing material is used with a combined frontal area of more than eighteen square feet shall not have a common exhaust.

(c) The fan rotating element shall be nonferrous or nonsparking or the casing

shall consist of or be lined with such material. There shall be ample clearance

between the fan rotating element and fan casing to avoid a fire by friction,

necessary allowance being made for ordinary expansion and loading to prevent

contact between moving parts and the duct or fan housing. Fan blades shall be

mounted on a shaft sufficiently heavy to maintain proper alignment even when the blades of the fan are heavily loaded, the shaft preferably to have bearings

outside the duct and booth. All bearings shall be of the self-lubricating type,

or lubricated from outside the duct.

(d) Electric motors driving exhaust fans shall not be placed inside booths or

ducts.

(e) Belts shall not enter duct or booth unless belt and pulley within the duct

or booth are completely enclosed.

(f) Where ductwork passes through a combustible roof or wall, the roof or wall

shall be protected at the point of penetration by open space or fire resistive

material between the duct and the roof or wall.

(g) When ducts pass through firewalls, they shall be provided with automatic

fire dampers on both sides of the wall, except that 3/8-inch steel plates may be

used in lieu of automatic fire dampers for ducts not exceeding 18 inches in

diameter.

(h) Exhaust ducts shall be constructed of steel and shall be substantially

supported. If dampers are installed, they shall be maintained so that adequate

airflow is maintained at all times the ventilating system is in operation. When

spray booths are not in use and it is necessary to shut off ducts,

noncombustible removable covers completely closing ducts may be used.

(i) Exhaust ducts shall be protected against mechanical damage and have a

clearance from unprotected combustible construction or other combustible

material of not less than 18 inches, except if combustible construction is

provided with the following protection applied to all surfaces within 18 inches,

clearances may be reduced to the distance indicated:

(1) 28 gauge sheet metal on 1/4-inch asbestos mill

board or equivalent.................................. 12 inches

(2) 28 gauge sheet metal on 1/8-inch asbestos mill

board spaced out one-inch on noncombustible spacers

or equivalent......................................... 9 inches

(3) 22 gauge sheet metal on 1-inch Rockwool bats

reinforced with wire mesh or the equivalent........... 3 inches

(4) Where ducts are protected with an approved automatic sprinkler system,

properly maintained; the clearance may be reduced to 6 inches.

(j) The spray booth exhaust discharge point shall be not less than six feet from

any combustible exterior wall or roof nor discharge in the direction of any

combustible construction or unprotected opening in any noncombustible exterior

wall within 25 feet.

(k) Freshly sprayed articles shall be dried only in spaces provided with

adequate ventilation to prevent the accumulation of flammable vapors. In the

event adequate and reliable ventilation is not provided such drying spaces shall

be considered a spraying area.

## Flammable and Combustible Liquids--Storage and Handling.

(a) The storage of flammable or combustible liquids in connection with spraying

operations shall conform to the requirements of Article 141, where applicable.

(b) Bulk storage of flammable or combustible liquids shall be in a separate,

properly constructed building detached from other important buildings or cut off

from them by construction having at least one-hour fire resistance rating.

NOTE: Lesser quantities of flammable or combustible liquids may be stored for

use within a building under conditions meeting the other provisions of this

section.

(c) The quantity of flammable and combustible liquids kept in the vicinity of

spraying operations outside an inside storage room or storage cabinet in any one

fire area shall not exceed the greater of: (1) a supply for one day or one

shift; (2) 25 gallons of Class IA liquids in containers, and 120 gallons of

Class IB, IC, II or IIIA liquids in containers, or (3) one approved portable

tank not exceeding 660 gallons of Class IB, IC, II, or IIIA liquids.

(d) Closed containers, approved portable tanks, approved safety cans, or a

properly arranged system of piping shall be used for transporting flammable or

combustible liquids. Open or glass containers shall not be used for

transportation or storage.

(e) The withdrawal of flammable or combustible liquids from containers and the

filling of containers, including portable mixing tanks, shall be done only in a

suitable mixing room or in a spraying area when the ventilating system is in

operation. Precautions shall be taken to protect against liquid spillage and

sources of ignition.

(f) Except as provided in (h), the withdrawal of flammable or combustible

liquids from containers having a capacity of greater than 60 gallons shall be by

approved pumps.

(g) Containers supplying spray nozzles shall be of closed type or provided with

metal covers kept closed. Containers not resting on floors shall be on

substantial supports or suspended by wire cables. Containers supplying spray

nozzles by gravity flow shall not exceed 10 gallons capacity.

(h) Original shipping containers shall not be subjected to air pressure for

supplying spray nozzles. Pressure vessels supplying spray nozzles shall be of

limited capacity, not exceeding that necessary for one day's operation; shall be

designed and approved for such use; shall be provided with a visible pressure

gauge; and shall be provided with a relief valve; all in conformance with the

Unfired Pressure Vessel Safety Orders.

(i) Containers under pressure supplying spray nozzles, air storage tanks and

coolers shall conform to the standards of the Unfired Pressure Vessel Safety

Orders for construction, tests and maintenance.

(j) All containers or piping to which is attached a hose or flexible connection

shall be provided with a shutoff valve at the connection. Such valves shall be

kept shut when spraying operations are not being conducted.

EXCEPTION: When a circulating system is used and it is provided with an

automatically operated anti-runaway control.

(k) When a pump is used to deliver products, automatic means shall be provided

to prevent pressure in excess of the design working pressure of accessories,

piping and hose.

(l) All pressure hose and couplings shall be inspected at regular intervals

appropriate to the service. With the hose extended, the hose and couplings shall

be tested using the "in service maximum operating pressures." Any hose showing material deteriorations, signs of leakage or weakness in its carcass or at the couplings shall be withdrawn from service.

(m) Unless flammable and combustible liquid piping, hose and equipment have been designed to meet the requirements of high pressure processes (those employing pressures in excess of 100 psig) such equipment shall not be used for this purpose.

(n) If flammable or combustible liquids are supplied to spray nozzles by

positive displacement pumps, means shall be provided to prevent the discharge

pressure exceeding the safe operating pressure of the system. Any discharge

shall be to a safe location.

(o) Piping systems conveying flammable or combustible liquids shall be of steel

or other material having comparable properties of resistance to heat and

physical damage; they shall be so installed that a rupture of the system for any

reason is unlikely. Piping systems shall be properly bonded and grounded.

(p) Whenever flammable or combustible liquids are transferred from one container to another, both containers shall be effectively bonded and grounded to

dissipate static electricity.

(q) If a spray liquid heater is used, it shall be low-pressure, steam or hot

water type, or electric. If electric, it shall be approved and listed for the

specific location in which it is used. (See Section 5449.) Heaters shall not be

located in spray booths nor other locations subject to the accumulation of

deposits or combustible residue. Agitators, if used, shall be driven by

compressed air, water, or low-pressure steam, or electric. If powered by an

electric motor, the motor shall conform to the requirements of Section 5449.

## Fire Protection.

(a) In sprinklered buildings, the automatic sprinkler system in rooms containing

spray application operations shall conform to Article 159, and in unsprinklered

buildings where sprinklers are installed only to protect spraying areas, the

installation shall conform to such standards insofar as they may be applicable.

Sprinkler installations shall also conform to the provisions of this Section.

Sprinkler heads shall be located so as to provide water distribution throughout

the entire booth.

(b) Water supply for sprinklers in rooms containing spray finishing operations

shall be sufficient to supply all sprinklers likely to open in one fire without

depleting the available water for use in hose streams.

NOTE: Where sprinklers are installed to protect spraying areas only, water may

be furnished from the domestic supply.

(c) Where automatic sprinklers protect each spray booth (together with its

connecting exhaust) they shall be under an accessibly located separate outside

stem and yoke (OS&Y) sub-control valve. Sprinkler systems in stacks or ducts

shall be automatic and of a type not subject to freezing.

(d) Sprinklers (heads) protecting spraying areas shall be kept as free from

deposits as practical by cleaning daily if necessary.

(e) Where automatic sprinkler protection is not available, a spray booth and its

exhaust ducts shall be protected with an extinguishing system installed so as to

conform either to Article 160, Article 161 or Article 162.

## Fixed Extinguishing Systems.

(a) Scope and Application.

(1) This Section applies to all fixed extinguishing systems except for automatic

sprinkler systems which are covered by Section.

(2) This Section also applies to fixed systems, but which, by means of their operation, may expose employees to possible injury, death, or adverse health consequences caused by the extinguishing agent. Such systems are only subject to the requirements of subsection (b)(4) through (b)(7) and (c) of this Section.

(3) Systems otherwise covered in subsection (a)(2) of this Section which are

installed in areas with no employee exposure are exempted from the requirements

of this section.

(b) General Requirements.

(1) Fixed extinguishing system components and agents shall be designed and

approved for use on the specific fire hazards they are expected to control or

extinguish.

(2) If for any reason a fixed extinguishing system becomes inoperable, the

company shall notify employees and take the necessary temporary precautions to assure their safety until the system is restored to operating order. Any defects

or impairments shall be properly corrected by trained personnel.

(3) The company shall provide a distinctive alarm or signaling system which

complies with Article 165 and is capable of being perceived above ambient noise

or light levels, on all extinguishing systems in those portions of the workplace

covered by the extinguishing system to indicate when the extinguishing system is

discharging. Discharge alarms are not required on systems where discharge is

immediately recognizable.

(4) The company shall provide effective safeguards to warn employees against

entry into discharge areas where the atmosphere remains hazardous to employee safety or health.

(5) The company shall post hazard warning or caution signs at the entrance to,

and inside of, areas protected by fixed extinguishing systems which use agents

in concentrations known to be hazardous to employee safety and health.

(6) The company shall assure that fixed systems are inspected annually by a

person knowledgeable in the design and function of the system to assure that the

system is maintained in good operating condition.

(7) The company shall assure that the weight and pressure of refillable

containers is checked at least semi-annually. If the container shows a loss in

net content or weight of more than 5 percent, or a loss in pressure of more than

10 percent, it shall be subjected to maintenance.

(8) The company shall assure that factory charged nonrefillable containers

which have no means of pressure indication are weighed at least semi-annually.

If a container shows a loss in net weight of more than 5 percent it shall be

replaced.

(9) The company shall assure that inspection and maintenance dates are recorded on the container, on a tag attached to the container, or in a central location. A record of the last semi-annual check shall be maintained until the container is checked again or for the life of the container, whichever is less.

(10) The company shall train employees designated to inspect, maintain,

operate, or repair fixed extinguishing systems and annually review their

training to keep them up to date in the functions they are to perform.

(11) The company shall not use chlorobromomethane or carbon tetrachloride as an extinguishing agent where employees may be exposed.

(12) The company shall assure that systems installed in the presence of

corrosive atmospheres are constructed of non-corrosive material or otherwise

protected against corrosion.

(13) Automatic detection equipment shall be approved, installed and maintained

(14) The company shall assure that all systems designed for and installed in

areas with climatic extremes shall operate effectively at the expected extreme

temperatures.

(15) The company shall assure that at least one manual station is provided for

discharge activation of each fixed extinguishing system.

(16) The company shall assure that manual operating devices are identified as

to the hazard against which they will provide protection.

(17) The company shall provide and assure the use of the personal protective

equipment needed for immediate rescue of employees trapped in hazardous

atmospheres created by an agent discharge.

(c) Total Flooding Systems with Potential Health and Safety Hazards to

Employees.

(1) The company shall provide an emergency action plan in accordance for each area within a workplace that is protected by a total flooding system which provides agent concentrations exceeding the maximum safe levels

(2) Systems installed in areas where employees cannot enter during or after the

system's operation are exempt from the requirements of Subsection (c) of this

Section.

(3) On all total flooding systems the company shall provide a pre-discharge

employee alarm which complies with Article 165, and is capable of being

perceived above ambient light or noise levels before the system discharges,

which will give employees time to safely exit from the discharge area prior to

system discharge.

(4) The company shall provide automatic actuation of total flooding systems by

means of an approved fire detection device installed and interconnected with a

pre-discharge employee alarm system to give employees time to safely exit from

the discharge area prior to system discharge.

## Fixed Extinguishing Systems; Dry Chemical.

(a) Scope and Application.

(1) This Section applies to all fixed extinguishing systems, using dry chemical

as the extinguishing agent. These systems shall also comply with Article 160.

(2) When dry chemical extinguishing systems are provided they shall meet the

design requirements of the National Fire Protection Association's "Standard for

Dry Chemical Extinguishing Systems" NFPA No. 171980 and the requirements of this section.

(b) Specific Requirements.

(1) The company shall assure that dry chemical agents are compatible with any

foams or wetting agents with which they are used.

(2) The company may not mix together dry chemical extinguishing agents of

different compositions. The company shall assure that dry chemical systems are

refilled with the chemical stated on the approval nameplate or an equivalent

compatible material.

(3) When dry chemical discharge may obscure vision, the company shall provide a pre-discharge employee alarm which complies with Article 165 and which will give employees time to safely exit from the discharge area prior to system discharge.

(4) The company shall sample the dry chemical supply of all but stored pressure

systems at least annually to assure that the dry chemical supply is free of

moisture which may cause the supply to cake or form lumps.

(5) The company shall assure that the rate of application of dry chemicals is

such that the designed concentration of the system will be reached within 30

second of initial discharge.

## Fixed Extinguishing Systems, Gaseous Agents

## Gaseous Systems.

(a) Scope and Application.

(1) Scope. This Section applies to all fixed extinguishing systems, using a gas

as the extinguishing agent. These systems shall also comply with Article 160. In

some cases, the gas may be in a liquid state during storage.

(2) Application. The requirements of Subsections (b)(5) and (b)(6) shall apply

only to total flooding systems.

(b) General Requirements.

(1) When carbon dioxide extinguishing systems are provided they shall meet the

design, inspection, maintenance, and instruction requirements of the National

Fire Protection Association's "Standard on Carbon Dioxide Extinguishing Systems" NFPA No. 121977.

(2) In any proposed use of carbon dioxide where there is a possibility that

employees may be trapped in, or enter into atmospheres made hazardous by a

carbon dioxide discharge suitable safeguards shall be provided to insure prompt

evacuation of and to prevent entry into such atmospheres and also to provide

means for prompt rescue of any trapped personnel. Suitable safeguards include

personnel training, warning signs, discharge alarms, predischarge alarms and

breathing apparatus any one or more of which may be necessary for particular

carbon dioxide extinguishing system installation.

(3) Agents used for initial supply and replenishment shall be of the type

approved for the system's application. Carbon dioxide obtained by dry ice

conversion to liquid is not acceptable unless it is processed to remove excess

water and oil.

(4) Except during overhaul, the company shall assure that the designed

concentration of gaseous agents is maintained until the fire has been

extinguished or is under control.

(5) Employees shall not be exposed to toxic levels of gaseous agent or its

decomposition products.

(6) The company shall assure that the designed extinguishing concentration is

reached within 30 seconds of initial discharge.

(f) An adequate supply of suitable portable fire extinguishers shall be

installed near all spraying areas.

## Portable Fire Extinguishers.

(a) Scope and Application. The requirements of this Section apply to the

placement, use, maintenance, and testing of portable fire extinguishers provided for the use of employees. Section (d) of this section does not apply to

extinguishers provided for employee use on the outside of workplace buildings or structures. Where extinguishers are provided but are not intended for employee use and the company has an emergency action plan and a fire prevention plan which meet the requirements.

(b) Exemptions.

(1) Where the company has established and implemented a written fire safety

policy which requires the immediate and total evacuation of employees from the

workplace upon the sounding of a fire alarm signal and which includes an

emergency action plan and a fire prevention plan which meet the requirements and when extinguishers are not available in the workplace, the company is exempt from all requirements of this section unless a specific Section in Title 8 requires that a portable fire extinguisher be provided.

(2) Where the company has an emergency action plan meeting the requirements which designates certain employees to be the only employees

authorized to use the available portable fire extinguishers, and which requires

all other employees in the fire area to immediately evacuate the affected work

area upon the sounding of the fire alarm, the company is exempt from the

distribution requirements in Section (d) of this Section.

(c) General Requirements.

(1) The company shall provide portable fire extinguishers and shall mount,

locate and identify them so that they are readily accessible to employees

without subjecting the employees to possible injury.

(2) Only approved portable fire extinguishers shall be used to meet the

requirements of this section.

(3) The company shall not provide or make available in the workplace portable

fire extinguishers using carbon tetrachloride or chlorobromomethane

extinguishing agents.

(4) The company shall assure that portable fire extinguishers are maintained in

a fully charged and operable condition and kept in their designated places at

all times except during use.

(5) The company shall permanently remove from service by January 1, 1982, all soldered or riveted shell self-generating soda acid or self-generating foam or

gas cartridge water type portable fire extinguishers which are operated by

inverting the extinguisher to rupture the cartridge or to initiate an

uncontrollable pressure generating chemical reaction to expel the agent.

(d) Selection and Distribution.

(1) Where portable fire extinguishers are provided for employee use, they shall

be selected and distributed based on the classes of anticipated work place fires

and on the size and degree of hazard which would affect their use.

(2) The company shall distribute portable fire extinguishers for use by

employees on Class A fires so that the travel distance for employees to any

extinguisher is 75 feet (22.9m) or less.

(3) The company may use uniformly spaced standpipe systems or hose stations connected to a sprinkler system installed for emergency use by employees instead of Class A portable fire extinguishers, provided that such systems meet the respective requirements, that they provide total coverage

of the area to be protected, and that employees are trained at least annually in

their use.

(4) The company shall distribute portable fire extinguishers for use by

employees on Class B fires so that the travel distance from the Class B hazard

area to any extinguisher is 50 feet (15.2m) or less.

(5) The company shall distribute portable fire extinguishers used for Class C

hazards on the basis of the appropriate pattern for the existing Class A or

Class B hazards.

(6) The company shall distribute portable fire extinguishers or other

containers of Class D extinguishing agent for use by employees so that the

travel distance from the combustible metal working area to any extinguishing

agent is 75 feet (22.9m) or less. Portable fire extinguishers for Class D

hazards are required in those combustible metal working areas where combustible

metal powders, flakes, shavings, or similarly sized products are generated a

least once every two weeks.

(e) Inspection, Maintenance and Testing.

(1) The company shall be responsible for the inspection, maintenance and

testing of all portable fire extinguishers in the workplace.

(2) Portable extinguishers or hose used in lieu thereof under Subsection (d)(3)

of this Section shall be visually inspected monthly.

(3) Portable fire extinguishers shall be subjected to an annual maintenance

check. Stored pressure extinguishers do not require an internal examination. The

company shall record the annual maintenance date and retain this record for one

year after the last entry or the life of the shell, whichever is less. The

record shall be available to the Chief upon request.

(4) Stored pressure dry chemical extinguishers that require a 12-year

hydrostatic test shall be emptied and subjected to applicable maintenance

procedures every 6 years. Dry chemical extinguishers having non-refillable

disposable containers are exempt from this requirement. When recharging or

hydrostatic testing is performed, the 6-year requirement begins from that date.

(5) Alternate equivalent protection shall be provided when portable fire

extinguishers are removed from service for maintenance and recharging.

(f) Hydrostatic Testing.

(1) The company shall assure that hydrostatic testing is performed by trained

persons with suitable testing equipment and facilities.

(2) The company shall assure that portable extinguishers are hydrostatically

tested at the intervals listed in Table L-1 of this Section, except under any of

the following conditions:

(A) when the unit has been repaired by soldering, welding, brazing, or use of

patching compounds;

(B) when the cylinder or shell threads are damaged;

(C) when there is corrosion that has caused pitting, including corrosion under

removable name plate assemblies;

(D) when the extinguisher has been burned in a fire; or

(E) when a calcium chloride extinguishing agent has been used in a stainless

steel shell.

Table L-1

Test

Interval

Type of Extinguishers            	        (years)

Soda acid (soldered brass shells)

(until 1/1/82)................................ 			(1)

Soda acid (stainless steel shell)............... 	5

Cartridge operated water and/or antifreeze......	5

Stored pressure water and/or antifreeze......... 	5

Wetting agent................................... 		5

Foam (soldered brass shells) (until 1/1/82)... 	(1)

Foam (stainless steel shell).................... 		5

Aqueous Film Forming Foam (AFFF)................ 5

Loaded stream................................... 		5

Dry chemical with stainless steel............... 	5

Carbon dioxide.................................. 		5

Dry chemical, stored pressure, with mild steel,

brazed brass or aluminum shells.............. 	12

Dry chemical, cartridge or cylinder operated,

with mild steel shells......................... 		12

Halon 1211..................................... 		12

Halon 1301..................................... 		12

Dry powder, cartridge or cylinder operated

with mild steel shells......................... 		12

1 Extinguishers having shells constructed of copper or brass joined by soft

solder or rivets shall not be hydrostatically tested and shall be removed from

service by January 1, 1982 (Not permitted).

(3) In addition to an external visual examination, the company shall assure

that an internal examination of cylinders and shells to be tested is made prior

to the hydrostatic tests.

(4) The company shall assure that portable fire extinguishers are

hydrostatically tested whenever they show new evidence of corrosion or

mechanical injury, except under the conditions listed in subsection

(f)(2)(A)-(E) of this Section.

(5) The company shall assure that hydrostatic tests are performed on

extinguisher hose assemblies which are equipped with a shut-off nozzle at the

discharge end of the hose. The test interval shall be the same as specified for

the extinguisher on which the hose is installed.

(6) The company shall assure that carbon dioxide hose assemblies with a

shut-off nozzle are hydrostatically tested at 1,250 psi (8,620 kPa).

(7) The company shall assure that dry chemical and dry powder hose assemblies

with a shut-off nozzle are hydrostatically tested at 300 psi (2,070 kPa).

(8) Hose assemblies passing a hydrostatic test do not require any type of

recording or stamping.

(9) The company shall assure that hose assemblies for carbon dioxide

extinguishers that require a hydrostatic test are tested within a protective

cage device.

(10) The company shall assure that carbon dioxide extinguishers and nitrogen or carbon dioxide cylinders used with wheeled extinguishers are tested every 5

years at 5/3 of the service pressure as stamped into the cylinder. Nitrogen

cylinders which comply with 49 CFR 173.34(e)(15) may be hydrostatically tested every 10 years.

(11) The company shall assure that all stored pressure and Halon 1211 types of extinguishers are hydrostatically tested at the factory test pressure not to

exceed two times the service pressure.

(12) The company shall assure that acceptable self-generating type soda acid

and foam extinguishers are tested at 350 psi (2,410 kPa).

(13) Air or gas pressure may not be used for hydrostatic testing.

(14) Extinguishers shells, cylinders, or cartridges which fail a hydrostatic

pressure test, or which are not fit for testing shall be removed from service

and from the workplace.

(15) The equipment for testing compressed gas type cylinders shall be of the

water jacket type. The equipment shall be provided with an expansion indicator

which operates with an accuracy within one percent of the total expansion or

0.1cc of liquid.

(A) The equipment for testing non-compressed gas type cylinders shall consist of the following:

1. A hydrostatic test pump, hand or power operated, capable of producing not

less than 150 percent of the test pressure, which shall include appropriate check valves and fittings;

2. A flexible connection for attachment to fittings to test through the

extinguisher nozzle, test bonnet, or hose outlet, as is applicable; and

3. A protective cage or barrier for personal protection of the tester, designed

to provide visual observation of the extinguisher under test.

(16) The company shall maintain and provide upon request to the Chief of

Division evidence that the required hydrostatic testing of fire extinguishers

has been performed at the time intervals shown in Table L-1. Such evidence shall be in the form of a certification record which includes the date of the test,

the signature of the person who performed the test and the serial number, or the other identifier, of the fire extinguisher that was tested. Such records shall

be kept until the extinguisher is hydrostatically retested at the time interval

specified in Table L-1 or until the extinguisher is taken out of service.

(g) Training and Education.

(1) Where the company has provided portable fire extinguishers for employee use

in the workplace, the company shall also provide an educational program to

familiarize employees with the general principles of fire extinguisher use and

the hazards involved with incipient stage fire fighting.

(2) The company shall provide the education required in subsection (g) (1) of

this Section upon initial employment and at least annually thereafter.

(3) The company shall provide employees who have been designated to use firefighting equipment as part of an emergency action plan with training in the use of the appropriate equipment.

(4) The company shall provide the training required in subsection (g) (3) of

this Section upon initial assignment to the designated group of employees and at least annually thereafter.

## Operation and Maintenance.

(a) Spraying shall not be conducted outside of predetermined spraying areas and

all provisions of this Section applying to spraying areas shall be strictly

followed.

(b) High pressure hose conveying flammable or combustible material in "airless"

spray application operations shall be frequently inspected and properly

maintained. Hose and equipment shall be so located that in the event of a leak

or rupture, application material will not be discharged into any space having a

source of ignition.

(c) All spraying areas shall be kept free from the accumulation of deposits of

combustible residues. If residue accumulates to excess in booths, duct or duct

discharge points or other spraying areas, then all spraying operations shall be

discontinued until conditions are corrected.

NOTE: Combustible coverings (thin paper, plastic, etc.) and strippable coatings

may be used to facilitate cleaning operations in spray areas.

(d) Spray booths, spray rooms and similar locations shall be thoroughly cleaned

of combustible deposits on floors, walls, ceilings, and equipment before any

repairs involving the use of torches, electric arcs or sparks, or other source

of ignition are undertaken.

(e) Scrapers, spuds or other such tools used for cleaning purposes shall be of

non-sparking material.

(f) Residue scrapings and debris contaminated with residue shall be immediately

removed from premises and properly disposed of.

(g) Self-closing, hinged, metal waste cans shall be provided wherever rags or

waste are impregnated with sprayed material and all such rags or waste shall be

deposited therein immediately after use. The contents of waste cans shall be

properly disposed of at least once daily or at the end of each shift.

(h) Employees' clothing contaminated with sprayed material shall not be left on

the premises overnight unless kept in metal lockers.

(i) Solvents for cleaning operations shall have flash points above 100o F,

however, for cleaning spray nozzles and auxiliary equipment, solvents having

flash points not less than those normally used in spray operations may be used.

(j) Cleaning operations using flammable or combustible solvents shall be

conducted inside spray booths with ventilating equipment operated during

cleaning or in other adequately ventilated locations.

(k) Spray booths shall not be alternately used for different types of coating

materials, where the combination of materials may be conducive to spontaneous

ignition, unless all deposits of the first used material are removed from the

booth and exhaust ducts prior to spraying with the second.

(l) Unless spray booths are thoroughly cleaned before changing operations,

booths used for application of pyroxylin finishes shall not be used for other

purposes.

(m) Smoking shall be prohibited except in designated localities. "NO SMOKING"

sign shall be conspicuously posted where hazard from flammable vapors may be

reasonably expected.

## Fixed Electrostatic Apparatus.

(a) This Section shall apply to any equipment using electrostatically charged

elements for the atomization, charging and (or) precipitation of hazardous

materials for coatings on articles or for other similar purposes in which the

charging or atomizing device is attached to a mechanical support and is not

hand-held or manipulated.

(b) Electrostatic apparatus and devices used in connection with coating

operations shall be of approved types.

(c) Transformers, high voltage supply, control apparatus, and all other

electrical portions of the equipment, with the exception of high voltage grids,

electrodes and electrostatic atomizing heads and their connections, shall be

located outside of the spraying area or shall otherwise conform to the

requirements of Section Electrical and Other Sources of Ignition.

(d) Electrodes and electrostatic atomizing heads shall be supported in permanent

locations and shall be insulated from ground. Electrodes and electrostatic

atomizing heads which are permanently attached to their bases, supports, or

reciprocators shall be deemed to comply with this Section. Insulators shall be

nonporous. Fine wire elements when used shall be under tension at all times and

be of unkinked hardened steel or material of comparable strength.

(e) High voltage leads shall be properly insulated and protected from mechanical

injury or exposure to destructive chemicals. Any exposed element at high voltage

shall be effectively guarded against accidental contact or grounding. An

automatic means shall be provided for grounding the electrode system when the

primary of its high voltage supply is electrically deenergized for any reason.

(f) All insulators shall be kept clean and dry.

(g) A safe distance shall be maintained between goods being painted and

electrodes or electrostatic atomizing heads or conductors of at least twice the

sparking distance. A suitable sign indicating this safe distance shall be

conspicuously posted near the assembly.

(h) Goods being coated using this process shall be supported on conveyors or

hangers. The conveyors or hangers shall be so arranged as to assure that the

parts being coated are electrically connected to ground and to maintain safe

distances between the goods and the electrodes or electrostatic atomizing heads

at all times. Goods shall be supported to prevent swinging or movement which

would reduce the clearance to less than that specified in (h).

(i) Electrostatic apparatus shall be equipped with automatic means which will

rapidly de-energize and ground the high voltage elements under any of the

following conditions:

(1) Stoppage of ventilating fans or failure of ventilating equipment from any

cause.

(2) Stoppage of the conveyor carrying goods through the high voltage field.

(3) Occurrence of a ground or excessive current leakage at any point on the high

voltage system.

(4) Reduction of clearance below that specified in (g).

(5) De-energizing the primary of the power supply.

(j) Safeguards such as booths, fencing, railings or other means shall be so

placed about the equipment or incorporated therein that they, either by their

location or character or both, assure that a safe isolation of the process is

maintained from plant storage or personnel. Mechanical guards shall be at least

5 feet from processing equipment.

(k) All electrically conductive objects in the spraying area, except those

objects required by the process to be at high voltage, shall be adequately

grounded. This requirement shall apply to paint containers, wash cans, guards

and any other electrically conductive objects or devices in the area. The

equipment shall carry a prominent permanently installed warning regarding the

necessity for this grounding feature.

(l) All areas used for spraying, including the interior of the booth, shall be

protected by automatic sprinklers where this protection is available. Where this

protection is not available, other approved automatic extinguishing equipment

shall be provided.

## Electrostatic Hand Spraying Equipment.

(a) This Section shall apply to any equipment using electrostatically charged

elements for the atomization, charging and (or) precipitation of materials for

coatings on articles, or for other similar purposes in which the atomizing

device is hand-held and manipulated during the spraying operation.

(b) Electrostatic hand spray apparatus and devices used in connection with

coating operations shall be of approved types. The high voltage circuits shall

be designed so as to not produce a spark of sufficient intensity to ignite the

most hazardous of those vapor-air mixtures likely to be encountered, nor result

in appreciable shock hazard upon coming in contact with a grounded object under  all normal operating conditions.

(c) The electrostatically charged exposed elements of the hand gun shall be

capable of being energized only by an actuator which also controls the coating

material supply.

(d) Transformers, high voltage supply, control apparatus, and all other

electrical portions of the equipment shall be located outside of the spraying

area or shall otherwise conform to the requirements of Section Electrical and Other Sources of Ignition.

EXCEPTION: The hand gun and its connections to the power supply.

(e) The handle of the spray gun shall be electrically connected to ground by a

metallic connection and be so constructed that the operator in normal operating

position is in intimate electrical contact with the grounded handle to prevent

buildup of a static charge on the operator's body. Signs indicating the

necessity for grounding other persons entering the spraying area shall be

conspicuously posted.

Whenever gloves are worn by the operator during electrostatic hand spraying, the grounding contact between the operator and the grounded handle of the spray gun shall be maintained.

(f) All electrically conductive objects in the spraying area shall be grounded.

This requirement shall apply to paint containers, wash cans and any other

electrically conductive objects or devices in the area. The equipment shall

carry a prominent permanently installed warning regarding the necessity for this

grounding feature.

(g) Objects being coated shall be maintained in electrical contact with the

conveyor or other grounded support. Hooks shall be regularly cleaned to insure

this contact and areas of contact shall be sharp points or knife edges where

possible. Points of support of the object shall be concealed from random spray

where feasible and where the objects being sprayed are supported from a

conveyor, the point of attachment to the conveyor shall be so located as to not

collect spray material during normal operation.

(h) The electrical equipment shall be so interlocked with the ventilation of the

spraying area that the equipment cannot be operated unless the ventilation fans

are in operation.

## Drying, Curing or Fusion Apparatus.

(a) Drying, curing or fusion apparatus in connection with spray application of

flammable and combustible coatings shall conform to the Standard for Ovens and Furnaces, NFPA No. 86A1977, where applicable and shall also conform to the following subsections.

(b) Spray booths, rooms or other enclosures used for spraying operations shall

not alternately be used for the purpose of drying by any arrangement which will

cause a substantial increase in the surface temperature of the spray booth, room

or enclosure.

(c) Except as specifically provided in (d), drying, curing or fusion units

utilizing a heating system having open flames or which may produce sparks shall

not be installed in a spraying area, but may be installed adjacent thereto when

equipped with an interlocked ventilating system arranged to:

(1) Thoroughly ventilate the drying space before heating system can be started;

(2) Maintain a safe atmosphere at any source of ignition;

(3) Automatically shut down heating system in the event of failure of the

ventilating system.

(d) When automobile refinishing spray booths or enclosures are used for drying

using portable electrical infrared drying apparatus, the following shall apply:

(1) Interior (especially floors) of spray enclosures shall be kept free of

overspray deposits.

(2) During spray operations, the drying apparatus and electrical connections and

wiring thereto shall not be located within spray enclosure nor in any other

location where spray residue may be deposited thereon.

(3) Spraying apparatus, drying apparatus, and ventilating system of spray

enclosure shall be equipped with suitable interlocks so arranged that:

(A) Spraying apparatus cannot be operated while drying apparatus is inside spray enclosure.

(B) Spray enclosure will be purged of spray vapors for a period of not less than

three minutes before drying apparatus can be energized.

(C) Ventilating system will maintain a safe atmosphere within the enclosure

during the drying process and drying apparatus will automatically shut off in

the event of failure of the ventilating system.

(4) All electrical wiring and equipment of drying apparatus shall conform to the

applicable sections of the Electrical Safety Orders. Only equipment approved for

Class I, Division 2 locations shall be located within 18 inches of floor level.

All metallic parts of drying apparatus shall be electrically bonded and

grounded.

(5) Drying apparatus shall contain a prominently located permanently attached

warning sign indicating that ventilation shall be maintained during the drying

period and spraying shall not be so conducted in the vicinity that spray will

deposit on apparatus.

(e) Fusion facilities shall be ventilated.

## Electrical.

See section in safety manual

## Ventilation.

See section in safety manual

## Automobile Undercoating in Garages.

Undercoating spray operations shall conform to all requirements of this Article

pertaining to spray finishing operations.

EXCEPTION: Automobile undercoating operations in garages, conducted in areas having adequate natural or mechanical ventilation, are exempt from the

requirements pertaining to spray coating operations, when undercoating materials not more hazardous than kerosene (as classified by Underwriters Laboratories in respect to fire hazard rating 30-40) are used, or undercoating materials using only solvents having a flash point in excess of 100o F(37.8o C) are used, and no open flames or other sources of ignition are within 20 feet while such operations are conducted.

## Powder Coating.

(a) This section shall apply to processes in which combustible dry powders are

applied such as:

(1) Fluidized bed.

(2) Electrostatic fluidized bed.

(3) Powder spray guns.

(4) Electrostatic powder spray guns.

(b) Powder coating operations shall be confined to properly designed enclosures

protected with automatic fire extinguishing systems.

(c) Powder shall be effectively confined by conducting coating operations

within:

(1) Completely enclosed, adequately ventilated rooms of noncombustible

construction with smooth surfaces designed to prevent accumulation of powder and to facilitate cleaning, or

(2) Adequately ventilated spray booths and by using effectively enclosed,

adequately ventilated containers (tanks, bins, etc.) of noncombustible material.

(d) Electrical equipment shall conform to the requirements of the Electrical

Safety Orders.

(e) Powder transport, application and recovery equipment shall be grounded.

(f) Ventilation requirements shall conform to the provisions of Section 5153 and

5143.

(g) All areas including horizontal surfaces such as ledges, beams, pipes, hoods

and booth floors shall be periodically cleaned to prevent the accumulation of

powder.

(h) Surfaces shall be cleaned in such manner as to avoid scattering powder or

creating powder clouds. Vacuum sweeping equipment where used, shall be of a type

approved for use in hazardous locations.

(i) Care shall be exercised to prevent tramp iron or spark producing material

from being introduced into the powders being applied. Magnetic and filter type

separators are recommended.

(j) Smoking shall be prohibited except in designated localities. "NO SMOKING"

signs shall be conspicuously posted where hazard from flammable vapors or

combustible powders are normally present.

(k) The provisions of Section 5454 and this section shall apply to fixed

electrostatic equipment, except that electrical equipment not covered therein

shall conform to (d) and (e) of this Section.

(l) The provisions of Section 5455 and this Section shall apply to electrostatic

hand guns when used in powder coating. The high voltage circuits shall be

designed so as not to produce a spark of sufficient intensity to ignite any

powder-air mixtures likely to be encountered. The electrical equipment not

covered by Section 5455 shall comply with (d) and (e) of this Section.

(m) Electrostatic fluidized beds and associated equipment shall be of approved

types. The high voltage circuits shall be so designed that any discharge

produced when the charging electrodes of the bed are approached, or contacted by

a grounded object shall not be of sufficient intensity to ignite any powder-air

mixture likely to be encountered, nor result in an appreciable shock hazard.

(n) Transformers, high voltage supply, control apparatus and all other

electrical portions of the equipment, with the exception of the charging

electrodes and their connections to the power supply shall be located outside of

the powder coating area or shall otherwise conform to the requirements (d) and

(e) of this Section.

(o) All electrically conductive objects within the powder coating area shall be

grounded. The powder coating equipment shall carry a prominent, permanently

installed warning regarding the necessity for grounding these objects.

(p) Objects being coated shall be maintained in electrical contact with the

conveyor or other support in order to insure proper grounding. Hangers shall be

regularly cleaned to insure effective contact and areas of contact shall be

sharp points or knife edges where possible.

(q) The electrical equipment shall be so interlocked with the ventilation system

that the equipment cannot be operated unless the ventilation fans are in

operation.

## Organic Peroxides and Dual Component Coatings.

(a) Extreme care shall be exercised at all times to prevent the contamination of

organic peroxide initiators with any foreign substance. Only spray guns and

related handling equipment specifically manufactured for use with organic

peroxides shall be used. Separate pressure vessels and inserts specific for the

application shall be used for the resin and for the organic peroxide and they

shall not be interchanged.

(b) Organic peroxide pressure tank inserts shall be constructed of stainless

steel, polyethylene, or other chemically nonreactive materials.

(c) Extreme care shall be exercised to prevent any mixing of dusts or overspray

residues resulting from the sanding or spraying of finishing materials

containing organic peroxides with other materials. Such mixing may result in a

spontaneous fire or explosion.

(d) All spilled peroxides shall be promptly removed so there are no residues.

Spilled material may be absorbed by using a noncombustible absorbent and then

promptly disposed of in accordance with the manufacturer's recommendation.

(e) Organic peroxides shall be stored in a cool, detached building apart from

other finishing materials, and only minimum daily requirements shall be brought

to the processing area; such material remaining at the spraying station at the

end of a day's operations shall be carefully disposed of. Organic peroxides

shall be kept away from all sources of heat including steam pipes, radiators,

open flames or sparks and solar radiation.

(f) Extreme care shall be exercised in handling organic peroxides to avoid shock

and friction which can cause decomposition and violent reaction.

(g) Organic peroxides shall not be mixed directly with any accelerators or

promoters as violent decomposition or explosion may result.

(h) Smoking shall be prohibited and "No Smoking" signs shall be prominently

displayed and only nonsparking tools shall be used in any area where organic

peroxides are stored, mixed or applied.

(i) Only specifically trained personnel shall be permitted to work with these

materials.

(j) Spraying with organic peroxides and other dual-component coatings shall be

conducted only in sprinkler-equipped spray booths.

(k) All wetted portions of organic peroxide handling equipment shall be

constructed of stainless steel (300 series), polyethylene, Teflon (registered

trademark) or other materials which are specifically recommended for the

application.